SPECIFICATIONS FOR SUPPLY & INSTALLATION OF SURGE PROTECTION DEVICES FOR

…………… WATER SUPPLY SCHEME

Revised on  02-09-2017

TABLE OF CONTENTS

1.		General Requirements																			6ai - 2

2.		Multi MOV Surge Diverters																	6ai - 3

3.		Surge Ratings																						6ai - 3

4.		Tests																									6ai - 3

5.		Material and Dimensions of Bonding Components 									6ai - 4

6.		Quality Assurance 																				6ai - 4

7.		Specifications for Spds																			6ai - 4

# 8.		Questionnaire for Surge Protectors															6ai - 7

GOVERNMENT OF THE DEMOCRATIC SOCIALIST REPUBLIC OF SRI LANKA

MINISTRY OF WATER SUPPLY AND DRAINAGE

NATIONAL WATER SUPPLY AND DRAINAGE BOARD

SUPPLY AND INSTALLATION OF SURGE PROTECTION DEVICES AND ACCESSORIES FOR ...................... WATER SUPPLY SCHEME

CONTRACT NO: ...............................

- GENERAL REQUIREMENTS

This specification is for supply and installation of surge protection devices to protect electrical system and equipment in the above treatment plant, against various over voltages and impulse currents such as lightning and switching surges.  The Surge Protecting Device (SPD) shall be fitted with necessary disconnecting devices in order not to interfere with other protective devices such as RCD, Fuse or Circuit Breakers in order to isolate the protected equipment from the installation in case of SPD failure.  SPD’s shall be installed in separate enclosure and connect the SPD with minimum possible length of cables. (maximum length of 50m bound wire is preferred)

The following IEC standards are applicable for the work.

IEC 61643		Low-voltage surge protective devices

- IEC 61643-1		Surge protective devices connected to low-voltage power 										distribution systems – Requirements and tests

- IEC 61643-12	Surge protective devices connected to low-voltage power 										distribution systems – Selection and application principles

- IEC 61643-21	Surge protective devices connected to low-voltage 												telecommunications and signalling networks – Performance

requirements and testing methods

- IEC 61643-22	Surge protective devices connected to low-voltage 												telecommunications and signalling networks – 	Selection and

application principles

- IEC 61643-311	Components for surge protective devices – Test specification

for gas discharge tubes (GDTs)

- IEC 61643-321	Components for surge protective devices – Test specification

for avalanche breakdown diodes (ABDs)

- IEC 61643-331	Components for surge protective devices – Test specification

for metal oxide varistors (MOVs)

- IEC 61643-341	Components for surge protective devices – Test specification

for thyristor surge supressors (TSSs)

- MULTI MOV Surge Diverters.

- MULTI MOV Surge diverters shall be designed to provide high energy surge diversion for individual phase power circuits and shall have following basic functions.

- In power systems in absence of surge: the SPD shall not have a significant influence on the operational characteristics of the system to which it is applied.

- In power systems during occurrence of surge: the SPD shall respond to surge by lowering its impedance and thus diverting surge current through it to limit the voltage to its protective level. The surge may initiate a power follow current through the SPD.

- In power systems after the occurrence of surge: the SPD recovers to a high-impedance state after the surges and extinguishes any possible power flow current.

- The units shall be capable of mounting at main power switch boards and major distribution boards.

- Surge diverters shall be tested according to IEC 61643 class 1 test & class II as specified under clause ‘Test’.

- In a systems design MULTI MOV surge diverters shall be utilized upstream of power surge filters for effective protection of sensitivity loads.

- Installation of surge protection devices shall be complied with TT system.

- Surge Ratings.

Multi MOVs of following rates shall be installed at the stages mentioned.

Stage											Rating of MOV

Main Incoming panel 					100 kA

Sub Incoming panel						  50 kA

Equipment level	    						  20 kA

- Tests

Surge protectors for main incoming panel/panels shall be tested according to IEC 61643-1

Class 1.

Surge protectors for sub incoming panel/panels shall be tested according to IEC 61643-1 Class II.

Test certificates of the above tests shall be submitted with the equipments

- Material and dimensions of bonding components

Material, dimensions and conditions of use shall comply with IEC 62305-3.  The minimum cross section for bonding components shall comply with Table 1 of IEC 62305-1.

- Quality Assurance

The indirect lightning protection system shall conform to the requirements and standards for lightning protection systems in accordance with IEC 62305 & IEC 61643.

- SPECIFICATIONS FOR SPDs

100kA SPD

| Description | Rating |
| --- | --- |
| Nominal Voltage/Phases | 400v/3 phase |
| Nominal Frequency | 50Hz |
| Rated load current | ………… |
| Nominal discharge current (8/20µs impulses) | 100 kA |
| Required class of testing | IEC 61643-1 Class I |
| Response time | Less than 25 ns |
| Voltage protection level | Less than 1.3 kV |
| Maximum continuous operating voltage | Not less than 270 V |
| Temperature range | Up to 80 0C |
| Residual voltage | As low as possible |
| Fuse | Include with high energy spark gap fuse |
| Thermal disconnect | Internal |
| Alarms | Audio/visual indications |
| AC system | TT system. |
| Protection rating | Shall comply the IEC 60529 |
| Short circuit protection | HRC fuse |
| Combination Arrestor | Suitable type |

50 kA SPD

| Description | Rating |
| --- | --- |
| Nominal Voltage/Phases | 400v/3 phase |
| Nominal Frequency | 50Hz |
| Rated load current | ………… |
| Nominal discharge current (8/20µs impulses) | 50 kA |
| Required class of testing | IEC 61643-1 Class II |
| Response time | Less than 25 ns |
| Voltage protection level | Less than 1.3 kV |
| Maximum continuous operating voltage | Not less than 270 V |
| Temperature range | Up to 80 0C |
| Residual voltage | As low as possible |
| Fuse | Include with high energy spark gap fuse |
| Thermal disconnect | Internal |
| Alarms | Audio/visual indications |
| AC system | TT system. |
| Protection rating | Shall comply the IEC 60529 |
| Short circuit protection | HRC fuse |
| Combination Arrestor | Suitable type |

20 kA SPD

| Description | Rating |
| --- | --- |
| Nominal Voltage/Phases | 400v/3 phase |
| Nominal Frequency | 50Hz |
| Rated load current | ………… |
| Nominal discharge current (8/20µs impulses) | 20 kA |
| Required class of testing | IEC 61643-1 Class II |
| Response time | Less than 25 ns |
| Voltage protection level | Less than 1.3 kV |
| Maximum continuous operating voltage | Not less than …….V |
| Temperature range | Up to 80 0C |
| Residual voltage | As low as possible |
| Fuse | Include with high energy spark gap fuse |
| Thermal disconnect | Internal |
| Alarms | Audio/visual indications |
| AC system | TT system. |
| Protection rating | Shall comply the IEC 60529 |
| Short circuit protection | HRC fuse |
| Combination Arrestor | Suitable type |

# QUESTIONNAIRE FOR SURGE PROTECTORS

| Description |  |
| --- | --- |
| - Make/Country of Manufacture |  |
| - Dimensions/Mounting |  |
| - Maximum operating voltage |  |
| - Nominal Discharge Current |  |
| - Maximal Discharge Current |  |
| - Max. lightning current by pole |  |
| - Residual Voltage |  |
| - Protection level |  |
| - Admissible short-circuit current |  |
| - Thermal disconnector |  |
| - Fuses |  |
| - Installation ground fault breaker |  |
| - Status of indication(Visual/Electrical) |  |
| - Operating Temperature |  |
| - Protection Class |  |
| - Housing material |  |
| - Standard Compliance |  |
| - Conductor size |  |
| - Conductor Color Code. |  |