**Specification for GRANULAR activated carbon**

**Revised from 18.06.2018**

**SPECIFICATION FOR GRANULAR ACTIVATED CARBON**

# GENERAL

# TABLE OF CONTENTS

 **PAGE NUMBER**

1 Ambient Conditions 8bh - 2

2 Suitability for Potable Water 8bh - 2

3 Definitions 8bh - 2

4 Inspection and Testing 8bh - 2

5 Marking 8bh - 3

6 Protection during Delivery 8bh - 3

7 Storing handling and hauling of Materials 8bh - 3

8 Manufacturer's Certificate 8bh - 4

9 Quality and workmanship 8bh - 4

10. Features and Benefits 8bh - 4

12. Technical Specification for Granular Activated Carbon 8bh - 5

**GENERAL**

**1 Ambient Conditions**

All materials shall be in every respect suitable for storage, use and operation in the conditions of temperature and humidity appertaining in Sri Lanka.

The annual average temperature is between 35°C while the relative humidity varies generally from 70% during the day to 90% at night.

**2 Suitability for Potable Water**

Granular Activated carbon will come into contact with potable water shall not constitute a toxic hazard, shall not support microbial growth.

### Definitions

The definitions given in the relevant standards which are referred to in the specification shall apply for the terms used in this specification.

**4 Inspection and Testing**

All materials shall be tested to the appropriate tests at the manufacturer’s premises and shall be supported by a test certificate from the manufacturer, for the conformity to the specified standards hereof.

The format for test certificate shall be in accordance with the format given in the Bidding Document.

The Manufacturer shall supply, furnish and prepare the necessary test samples of materials and supply necessary technical personnel labour, facilities, and appliances for such testing as may be required to be carried out in the manufacturer’s premises according to this specification. If there are no facilities at his own for making the prescribed tests, the Manufacturer shall arrange to perform such tests from an accredited testing Agency and shall bear all costs associated with such tests.

Manufacturer shall submit Product Conformity certificate for the conformity to the standards for the product specified in this specification.

The Contractor shall furnish the Engineer with all required facilities and space at Manufacturer’s cost for the inspection, testing and obtaining of such information, as he desires regarding the character of material in use and the progress and manner of the work.

Revised from 18.06.2018

The Engineer or his representatives and nominated Inspection Agency shall have full access to all parts of the plant that are concerned with the manufacturing, testing, furnishing or preparation of materials for the performance and testing of work under this Specification.

 Contractor shall be held responsible for the assuring the quality of the goods supplied by him up the final delivery point. Granular Activated Carbon is tested at the Employer’s final delivery point by the employer and goods shall conform to the relevant standard for the acceptance.

 **5. Marking**

All markings shall be legible and durable unless otherwise specified and shall be as specified in the Technical Specification.

**6. Protection During Delivery**

The contractor shall provide protection as approved by the Engineer, prior to the materials leaving the place of manufacture and shall maintain such protection until the items reach their destination in order to guard effectively against damage during transit and storage and the ingress of foreign matter inside the packages.

All details of the proposed method of providing such protection shall be submitted at the time of tendering.

The cost of providing protection shall be included in the unit prices offered in the Bills of Quantities.

**7. Storing, Handling and Hauling of Materials.**

All materials shall be stored in an approved location and in such a manner as to preserve their quality and condition.

Storage shall be in accordance with the manufacturer’s recommendation and shall be stored in a dry place with a proper packing.

Materials and components shall be handled in such a manner as to avoid any damage or contamination and in accordance with the recommendations of the manufacturers.

The contractor shall give instructions to the shipper on precautions to be followed in the handling of materials during loading, towage delivery and unloading and shall give particulars of these instructions to the purchaser.

**8. Manufacturer’s Certificate**

The Contractor shall supply to the Engineer a certificate stating that each item supplied has been subjected to the tests laid down herein and conforms in all respects to this Specification or such other Specification which has been submitted to and approved by the Engineer. In addition to this, contractor shall provide certificate for the conformity to the Standards (BSEN 12902:2009) from an independent testing agency mentioned in General condition of contract. Testing at Manufacturers factory by Employer will perform as specified.

**9. Quality and Workmanship**

The Bidder shall provide ISO 9001 : 2015 Quality Management System requirement certificate for Quality Assurance for the goods manufacturing factory from an accredited agency for Granular Activated Carbon. Accredited Agency shall be a member of International Accredited Forum (IAF) and shall have the authority for the accreditation of mentioned goods in their scope of accreditation. Scope of the production shall be clearly specified in the certificate. Manufacturer shall maintain the validity of this certificate during the contract Period. If the supply is made from several factories, ISO 9001 : 2015 certificates for quality management system requirement shall be submitted for each factory.

**10. Features and Benefits**

* Porous material manufactured from carbonaceous raw materials
* Meets AWWA B-604-12 standards/EN 12915:2009

Revised from 23.07.2018

## 11. Technical Specification for Granular Activated Carbon

**11.1 General Requirements**

All materials to be supplied under Bill no.1 of this contract shall conform to EN 12915:2009 or AWWA B 604-12, chemicals used for treatment of water for human consumption-granular activated carbon.

* 1. **Other Requirements**
		1. **Features Required**

 Granular Activated Carbon Used for Potable Water Supply shall comply with requirements as specified in following table.

Table 1 – Product Specification

|  |  |  |
| --- | --- | --- |
| **Parameter** | **Requirements** | **Test Method** |
| **A. Chemical requirements**  |  |  |
| Iodine number, mg/g of dry product | 900 min  | ASTM D4607, EN 12902: 1999 |
| Uniformity coefficient, UC | 1.4-2.2 | EN 12902: 1999 |
| **B. Impurities**  |  |  |
| Water soluble matter, %(w/w) | 3.0 max  | AWWA B600-96, EN 12902: 1999 |
| Moisture, %(w/w)  | 5 max | AWWA B600-96 EN 12902: 1999 |
| Ash, %(w/w)  | 15 max  | EN 12902: 1999 |
| Zinc, %(w/w) | 0.002 max | EN 12902: 1999 |
| **C. Physical Requirements**  |  |  |
| Ball pan hardness  | 75 min  | EN 12915: 1999 |
| Wet ability | 99 min  | EN 12915: 1999 |
| Bulk density, packed, kg/m³  | 180 min  | EN 12915: 1999 |
| **D. Toxic Substances**  | Maximum limit mg/kg of Product | Test Method  |
| Arsenic, As  | 10 | EN 12902: 1999 |
| Cadmium, Cd | 0.5  | EN 12902: 1999 |
| Chromium, Cr  | 5  | EN 12902: 1999 |
| Mercury, Hg  | 0.3 | EN 12902: 1999 |
| Nickel, Ni  | 5  | EN 12902: 1999 |
| Lead, Pb  | 5  | EN 12902: 1999 |
| Selenium, Se  | 3  | EN 12902: 1999 |
| Antimony, Sb  | 3  | EN 12902: 1999 |
| Cyanide, Cn  | 5  | EN 12902: 1999 |
| PAH  | 0.02  | EN 12902: 1999 |

* 1. **Transport and Storage**
		1. **Means of delivery**

The product shall be delivered in suitable paper sacks (10kg each bag) or suitable polypropylene bags (25 kg each bag). Bags should be stacked in rows with aisles between them and should be stored alone. In order that the purity of the product is not effected the means of delivery shall not have been used previously for different product or it shall have been specially cleaned and prepared before use.

* + 1. **Storage**

Granular Activated Carbon shall be stored in a building or compartment in a clean dry and well ventilated area.

Product shall be kept away from oxidants for fire resistant.(eg. Hydrogen peroxide, potassium permanganate, chlorates, Nitrates, Volatile solvents and moisture).

* 1. **Marking and Labeling**

Each package shall be marked legibly and indelibly with following information: (Letter height shall be 50 mm)

* 1. The name “Granular Activated Carbon” , trade name, trade mark and grade
	2. The net mass
	3. Name and address of the manufacturer
	4. Batch No.
	5. Date of manufacturing and date of expiry; and shall bear such other markings as requires by applicable laws
	6. Contract Number
	7. Statement “Product conforms to EN 12915-1:2009/AWWA B 604-12”
	8. **Sampling & Testing**

Sampling and Testing shall be in accordance with the EN 12902-1:2009

All Granular Activated Carbon shall comply with test in accordance with the requirement

of specification.

|  |  |  |
| --- | --- | --- |
| **Properties** | **Value** | **Method** |
| Abrasion Number (min) | 75 | ASTM D3802 |
| Moisture as Packed (max) | 5% | ASTM D2867 |
| Apparent Density (lbs./ ft³) | 31 | ASTM D2854 |
| Backwashed Apparent Density (lbs./ft³) | 27 | ASTM D2B54 |
| Mesh Sizegreater than 8 mesh (max) | 8 x 305% | U.S. Sieve |
| **Properties** | **Value** | **Method** |
| less than 30 mesh (max) | 5% |  |
| Typical Surface Area (m²/g) | 1,050 | BET N2 |
| Ash Content (max) | 12% | ASTM D2866 |
| Iodine Number (mg/g) | 900 | AWWA B604-12 |

* 1. **Physical Properties**

Physical Properties of Granular Activated Carbon used for potable water supply as

follows:

|  |  |  |
| --- | --- | --- |
| **No.** | **Physical Properties** | **Description** |
| 1. | Row material | Peat, bituminous schists, anthracite, wood, coconut |
| 2. | Presentation | Crushed, extruded |
| 3. | Appearance  | i. Black  |
|  |  | ii. Porous granular of irregular shape |
| 4. |  Granulometry | ES- 0.25-3mmUC- 1.4-2.2 |
| 5. | Apparent (compacted) density  | 0.2-.55 g.cm-3 |
|  |  |  |
| 6. | Specific Surface Area  | 600-2,500 m2.g-1 |

* 1. **Pre-Delivery Inspection and Evaluation**

It is the responsibility of the supplier to inform in advance the Engineer for inspection purposes during manufacturing and before delivery.

Engineer reserve the right to inspect and witness the testing of the product offered without any prior notice.

* 1. **Certification**

Manufacturer shall provide product conformity certificate issued by an Accredited Testing and Inspection Agency which is a member of the International Accreditation Forum (IAF).