## Inspection63
PRE QUALIFICATION OF PE PIPES & FITTINGS MANUFACTURE FOR WATER SUPPLY & SEWERAGE WORKS
DOCUMENT NO: PQ/PE/NWSDB/2016/01
INSPECTION REPORT
Manufacturer : |  | St.Anthony's Industries Group (Pvt.) Ltd.
Factory Address : |  | 113A, Raja Mawatha, Ekala,Ja-Ela
Material : |  | HDPE Pipes as per ISO 4427 - 2007
Size : |  | PE 100 PN16 DN63x5.8MM W.T SDR11 (Blue Colour)
Dimensions:-
Sr. No. | Outer Diameter (mm) by Vernier Calliper |  |  | Ovality (mm) Max. | Wall Thickness (mm) |  | Visual Appearance | Length (Mtr.)
[5 empty] | Min. | Max.
Standard | Min 63 | Max 63.4 |  | 1.5 | 5.8 | 6.5 | Shall be smooth | coil Pipes
01 | 63.1 |  |  | 63.39 | 6.1 | 6.45 | smooth
02 | 63.1 |  |  | 63.37 | 6.15 | 6.45
03 | 63.1 |  |  | 63.2467 | 6.15 | 6.45
Tests:-
Sr.No. | Tests |  | Requirement |  | Results |  |  | Remarks
Sample No.01
01 | Longitudinal Reversion Test Test Temp. 110 ± 2⁰C |  | ≤3% No effect on surface |  | 1.4% |  |  | satisfied
02 | Compounded Density at 23⁰C |  | ≥ 930 Kg/m³ |  | 948 |  |  | satisfied
03 | Elongation at Break |  | ≥ 350% |  | 423% |  |  | satisfied
04 | Thermal Stability (OIT) |  | ≥ 20 Minutes |  |  |  |  | satisfied
05 | Melt Flow Rate (MFR) at 190⁰C with 5.0 Kg Load. |  | Not more than 20% of value nominated by raw material supplier |  |  |  |  | satisfied
06 | Hydrostatic Strength 100 hrs at 20⁰C Induced Stress : 12.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
07 | Hydrostatic Strength 165 hrs at 80⁰C Induced Stress : 5.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
Note: Sample test only.
National Water Supply & Drainage Board
Eng. (Ms) A.S.Kaluarachchi |  |  | Eng.(Ms) Anusha Adhihetti |  |  | Eng.(Ms) G.G.S.Lekha
DGM (Development) |  |  | AGM (P&D-Doc) |  |  | CE(P&D-Doc)
Eng. (Ms) H.M.C.P.Herath |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  | (Ms) N.D.Yapa
CE(Water Reclamation) |  |  | Eng(P&D-Doc) |  |  | EA-Sp(P&D-Doc)
Bureau Veritas Lanaka (Pvt.) Ltd.
Mr. Akalanka Wickramatilake | [5 empty] | Eng. J.Karunaratne
| Manager Building & Infrastructure Services |  |  |  |  | Engineer (QA)
St. Anthony's Industries Group(Pvt.) Ltd.
Mr. Bhathiya Prabhath | [5 empty] | Mr. Amila Seneviratna
Assistant Manager (Quality Assurance) | [5 empty] | Senior Quality Assurance Officer

## Inspection63 (2)
PRE QUALIFICATION OF PE PIPES & FITTINGS MANUFACTURE FOR WATER SUPPLY & SEWERAGE WORKS
DOCUMENT NO: PQ/PE/NWSDB/2016/01
INSPECTION REPORT
Manufacturer : |  | St.Anthony's Industries Group (PVT)LTD
Factory Address : |  | 113A, Raja Mawatha, Ekala,Ja-Ela
Material : |  | HDPE Pipes As per ISO 4427 - 2007
Size : |  | PE 100 PN16 DN63x5.8MM W.T SDR11 (Blue Colour)
Dimensions:-
Sr. No. | Outer Diameter (mm) by Vernier Calliper |  |  | Ovality (mm) Max. | Wall Thickness |  | Visual Appearance | Length (Mtr.)
[5 empty] | Min. | Max.
Standard | Min 63 | Max 63.4 |  | 1.5 | 5.8 | 6.5 | Shall be smooth | coil Pipes
01 | 63.1 |  |  | 63.39 | 6.1 | 6.45 | smooth
02 | 63.1 |  |  | 63.37 | 6.15 | 6.45
03 | 63.1 |  |  | 63.2467 | 6.15 | 6.45
Tests:-
Sr.No. | Tests |  | Requirement |  | Results |  |  | Remarks
Sample No.01
01 | Longitudinal Reversion Test Test Temp. 110 ± 2⁰C |  | ≤3% No effect on surface |  | 1.4% |  |  | satisfied
02 | Compounded Density at 23⁰C |  | ≥ 930 Kg/m³ |  | 948 |  |  | satisfied
03 | Elongation at Break |  | ≥ 350% |  | 423% |  |  | satisfied
04 | Thermal Stability (OIT) |  | ≥ 20 Minutes |  |  |  |  | satisfied
05 | Melt Flow Rate (MFR) at 190⁰C with 5.0 Kg Load. |  | Not more than 20% of value nominated by raw material supplier |  |  |  |  | satisfied
06 | Hydrostatic Strength 100 hrs at 20⁰C Induced Stress : 12.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
01 | Hydrostatic Strength 165 hrs at 80⁰C Induced Stress : 5.4 Mpa |  | No failure of test piece during test period. |  | No failure of test piece during test period. |  |  | satisfied
Note: Sample test only.
National Water Supply & Drainage Board
Eng. (Ms) A.S.Kaluarachchi |  |  | Eng.(Ms) Anusha Adhihetti |  |  | Eng.(Ms) G.G.S.Lekha
DGM (Development) |  |  | AGM (P&D-Doc) |  |  | CE(P&D-Doc)
Eng. (Ms) H.M.C.P.Herath |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  | (Ms) N.D.Yapa
CE(Water Reclamation) |  |  | Eng(P&D-Doc) |  |  | EA-Sp(P&D-Doc)
St. Anthony's Industries Group(Pvt.) Ltd.
Mr. Bhathiya Prabhath | [5 empty] | Mr. Amila Seneviratna
Assistant Manager (Quality Assurance) | [5 empty] | Senior Quality Assurance Officer
-
-

## Inspection50
PRE QUALIFICATION OF PE PIPES & FITTINGS MANUFACTURE FOR WATER SUPPLY & SEWERAGE WORKS
DOCUMENT NO: PQ/PE/NWSDB/2016/01
INSPECTION REPORT
Manufacturer : |  | St.Anthony's Industries Group (PVT)LTD
Factory Address : |  | 113A, Raja Mawatha, Ekala,Ja-Ela
Material : |  | HDPE Pipes as per ISO 4427 - 2007
Size : |  | PE 100 PN16 DN50x4.6MM W.T SDR11 (Blue Colour)
Dimensions:-
Sr. No. | Outer Diameter (mm) by Vernier Calliper |  |  | Ovality (mm) Max. | Wall Thickness (mm) |  | Visual Appearance | Length (Mtr.)
[5 empty] | Min. | Max. |  |  | 0.66
Standard | Min 50 | Max 50.4 |  | 1.4 | 4.6 | 5.2 | Shall be smooth | coil Pipes
01 | 50.2 |  |  | 50.2733 | 4.8 | 5 | smooth
02 | 50.2 |  |  | 50.3333 | 4.8 | 4.9
03 | 50.2 |  |  | 50.3333 | 4.8 | 4.9
Tests:-
Sr.No. | Tests |  | Requirement |  | Results |  |  | Remarks
Sample No.01
01 | Longitudinal Reversion Test Test Temp. 110 ± 2⁰C |  | ≤3% No effect on surface |  | 2.2% |  |  | satisfied
02 | Compounded Density at 23⁰C |  | ≥ 930 Kg/m³ |  | 946 |  |  | satisfied
03 | Elongation at Break |  | ≥ 350% |  | 426% |  |  | satisfied
04 | Thermal Stability (OIT) |  | ≥ 20 Minutes
05 | Melt Flow Rate (MFR) at 190⁰C with 5.0 Kg Load. |  | Not more than 20% of value nominated by raw material supplier |  | 6.67% |  |  | satisfied
06 | Hydrostatic Strength 100 hrs at 20⁰C Induced Stress : 12.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
07 | Hydrostatic Strength 165 hrs at 80⁰C Induced Stress : 5.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
Note: Sample test only.
National Water Supply & Drainage Board
Eng. (Ms) A.S.Kaluarachchi |  |  | Eng.(Ms) Anusha Adhihetti |  |  | Eng.(Ms) G.G.S.Lekha
DGM (Development) |  |  | AGM (P&D-Doc) |  |  | CE(P&D-Doc)
Eng. (Ms) H.M.C.P.Herath |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  | (Ms) N.D.Yapa
CE(Water Reclamation) |  |  | Eng(P&D-Doc) |  |  | EA-Sp(P&D-Doc)
Bureau Veritas Lanaka (Pvt.) Ltd.
Mr. Akalanka Wickramatilake | [5 empty] | Eng. J.Karunaratne
| Manager Building & Infrastructure Services |  |  |  |  | Engineer (QA)
St. Anthony's Industries Group(Pvt.) Ltd.
Mr. Bhathiya Prabhath | [5 empty] | Mr. Amila Seneviratna
Assistant Manager (Quality Assurance) | [5 empty] | Senior Quality Assurance Officer

## Inspection50 (2)
PRE QUALIFICATION OF PE PIPES & FITTINGS MANUFACTURE FOR WATER SUPPLY & SEWERAGE WORKS
DOCUMENT NO: PQ/PE/NWSDB/2016/01
INSPECTION REPORT
Manufacturer : |  | St.Anthony's Industries Group (Pvt) Ltd
Factory Address : |  | 113A, Raja Mawatha, Ekala, Ja-Ela
Material : |  | HDPE Pipes As per ISO 4427 - 2007
Size : |  | PE 100 PN16 DN50x4.6MM W.T SDR11 (Blue Colour)
Dimensions:-
Sr. No. | Outer Diameter (mm) by Vernier Calliper |  |  | Ovality (mm) Max. | Wall Thickness |  | Visual Appearance | Length (Mtr.)
| Min | Max | Mean |  | Min. | Max. |  |  | 0.66
Standard | 50 | 50.4 |  | 1.4 | 4.6 | 5.2 | Shall be smooth | coil Pipes
01 | 50.2 |  |  | 50.2733 | 4.8 | 5 | smooth
02 | 50.2 |  |  | 50.3333 | 4.8 | 4.9
03 | 50.2 |  |  | 50.3333 | 4.8 | 4.9
Tests:-
Sr.No. | Tests |  | Requirement |  | Results |  |  | Remarks
Sample No.01
01 | Longitudinal Reversion Test Test Temp. 110 ± 2⁰C |  | ≤3% No effect on surface |  | 2.2% |  |  | satisfied
02 | Compounded Density at 23⁰C |  | ≥ 930 Kg/m³ |  | 946 |  |  | satisfied
03 | Elongation at Break |  | ≥ 350% |  | 426% |  |  | satisfied
04 | Thermal Stability (OIT) |  | ≥ 20 Minutes
01 | Melt Flow Rate (MFR) at 190⁰C with 5.0 Kg Load. |  | Not more than 20% of value nominated by raw material supplier |  | 6.67% |  |  | satisfied
06 | Hydrostatic Strength 100 hrs at 20⁰C Induced Stress : 12.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
02 | Hydrostatic Strength 165 hrs at 80⁰C Induced Stress : 5.4 Mpa |  | No failure of test piece during test period. |  | No failure of test piece during test period. |  |  | satisfied
Note: Sample test only.
National Water Supply & Drainage Board
Eng. (Ms) A.S.Kaluarachchi |  |  | Eng.(Ms) Anusha Adhihetti |  |  | Eng.(Ms) G.G.S.Lekha
DGM (Development) |  |  | AGM (P&D-Doc) |  |  | CE (P&D-Doc)
Eng. (Ms) H.M.C.P.Herath |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  | (Ms) N.D.Yapa
CE (Water Reclamation) |  |  | Eng (P&D-Doc) |  |  | EA-Sp (P&D-Doc)
St. Anthony's Industries Group(Pvt.) Ltd.
Mr. Bhathiya Prabhath | [5 empty] | Mr. Amila Seneviratna
Assistant Manager (Quality Assurance) | [5 empty] | Senior Quality Assurance Officer

## Inspection 40
PRE QUALIFICATION OF PE PIPES & FITTINGS MANUFACTURE FOR WATER SUPPLY & SEWERAGE WORKS
DOCUMENT NO: PQ/PE/NWSDB/2016/01
INSPECTION REPORT
Manufacturer : |  | St.Anthony's Industries Group (Pvt) Ltd | [7 empty] | 20
Factory Address : |  | 113A, Raja Mawatha, Ekala, Ja-Ela | [7 empty] | 25
32
40
Material : |  | HDPE Pipes as per ISO 4427 - 2007 | [7 empty] | 63
Size : |  | PE 100 PN16 DN40x3.7MM W.T SDR11 (Blue Colour) | [7 empty] | 75
90
Dimensions:- | [9 empty] | 110
Sr. No. | Outer Diameter (mm) by Vernier Calliper |  |  | Ovality (mm) Max. | Wall Thickness (mm) |  | Visual Appearance | Length (Mtr.) |  | 160
[5 empty] | Min. | Max. |  |  | 0.24 | 180
Standard | Min 40 | Max 40.4 |  | 1.4 | 3.7 | 4.2 | Shall be smooth | coil Pipes |  | 200
01 | 40.4 |  |  | 40.215 | 3.9 | 3.95 | smooth |  |  | 225
02 | 40.4 |  |  | 40.615 | 3.85 | 3.95 |  |  |  | 250
03 | 40.4 |  |  | 40.615 | 3.7 | 3.95 |  |  |  | 280
Tests:- | [9 empty] | 315
Sr.No. | Tests |  | Requirement |  | Results |  |  | Remarks |  | 355
[5 empty] | Sample No.01 |  |  |  |  | 400
01 | Longitudinal Reversion Test Test Temp. 110 ± 2⁰C |  | ≤3% No effect on surface |  | 1.7% |  |  | satisfied |  | 450
02 | Compounded Density at 23⁰C |  | ≥ 930 Kg/m³ |  | 947 |  |  | satisfied
03 | Elongation at Break |  | ≥ 350% |  | 721% |  |  | satisfied
04 | Thermal Stability (OIT) |  | ≥ 20 Minutes
05 | Melt Flow Rate (MFR) at 190⁰C with 5.0 Kg Load. |  | Not more than 20% of value nominated by raw material supplier
06 | Hydrostatic Strength 100 hrs at 20⁰C Induced Stress : 12.4 Mpa |  | No failure of test piece during test period.
07 | Hydrostatic Strength 165 hrs at 80⁰C Induced Stress : 5.4 Mpa |  | No failure of test piece during test period.
Note: Sample test only.
National Water Supply & Drainage Board
Eng. (Ms) A.S.Kaluarachchi |  |  | Eng.(Ms) Anusha Adhihetti |  |  | Eng.(Ms) G.G.S.Lekha
DGM (Development) |  |  | AGM (P&D-Doc) |  |  | CE(P&D-Doc)
Eng. (Ms) H.M.C.P.Herath |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  | (Ms) N.D.Yapa
CE(Water Reclamation) |  |  | Eng(P&D-Doc) |  |  | EA-Sp(P&D-Doc)
Bureau Veritas Lanaka (Pvt.) Ltd.
Mr. Akalanka Wickramatilake | [5 empty] | Eng. J.Karunaratne
| Manager Building & Infrastructure Services |  |  |  |  | Engineer (QA)
St. Anthony's Industries Group (Pvt.) Ltd.
Mr. Bhathiya Prabhath | [5 empty] | Mr. Amila Seneviratna
Assistant Manager (Quality Assurance) | [5 empty] | Senior Quality Assurance Officer

## Inspection 32
PRE QUALIFICATION OF PE PIPES & FITTINGS MANUFACTURE FOR WATER SUPPLY & SEWERAGE WORKS
DOCUMENT NO: PQ/PE/NWSDB/2016/01
INSPECTION REPORT
Manufacturer: |  | St.Anthony's Industries Group (PVT)LTD
Factory Address: |  | 113A, Raja Mawatha, Ekala, Ja-Ela
Material: |  | HDPE Pipes As per ISO 4427 - 2007
Size: |  | PE 100 PN16 DN32x3.0MM W.T SDR11 (Blue Colour)
Dimensions:-
Sr. No. | Outer Diameter (mm) by Vernier Calliper |  |  | Ovality (mm) Max. | Wall Thickness(mm) |  | Visual Appearance | Length (Mtr.)
[5 empty] | Min. | Max. |  |  | 0.192
Standard | Min 32 | Max 32.3 |  | 1.3 | 3 | 3.4 | Shall be smooth | coil Pipes
01 | 32.3 |  |  | 32.335 | 3.15 | 3.2 | smooth
02 | 32.3 |  |  | 32.43 | 3.1 | 3.15
03 | 32.3 |  |  | 32.38 | 3.15 | 3.2
Tests:-
Sr.No. | Tests |  | Requirement |  | Results |  |  | Remark
Sample No.01
01 | Longitudinal Reversion Test Test Temp. 110 ± 2⁰C |  | ≤3% No effect on surface |  | 2.1% |  |  | satisfied
02 | Compounded Density at 23⁰C |  | ≥ 930 Kg/m³ |  | 945
03 | Elongation at Break |  | ≥ 350% |  | 594% |  |  | satisfied
04 | Thermal Stability (OIT) |  | ≥ 20 Minutes |  |  |  |  | satisfied
05 | Melt Flow Rate (MFR) at 190⁰C with 5.0 Kg Load. |  | Not more than 20% of value nominated by raw material supplier |  | 5.56% |  |  | satisfied
06 | Hydrostatic Strength 100 hrs at 20⁰C Induced Stress : 12.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
07 | Hydrostatic Strength 165 hrs at 80⁰C Induced Stress : 5.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
Note: Sample test only.
National Water Supply & Drainage Board
Eng. (Ms) A.S.Kaluarachchi |  |  | Eng.(Ms) Anusha Adhihetti |  |  | Eng.(Ms) G.G.S.Lekha
DGM (Development) |  |  | AGM (P&D-Doc) |  |  | CE(P&D-Doc)
Eng. (Ms) H.M.C.P.Herath |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  | (Ms) N.D.Yapa
CE(Water Reclamation) |  |  | Eng(P&D-Doc) |  |  | EA-Sp(P&D-Doc)
Bureau Veritas Lanaka (Pvt.) Ltd.
Mr. Akalanka Wickramatilake | [5 empty] | Eng. J.Karunaratne
| Manager Building & Infrastructure Services |  |  |  |  | Engineer (QA)
St. Anthony's Industries Group(Pvt.) Ltd.
Mr. Bhathiya Prabhath | [5 empty] | Mr. Amila Seneviratna
Assistant Manager (Quality Assurance) | [5 empty] | Senior Quality Assurance Officer

## Inspection 32 (2)
PRE QUALIFICATION OF PE PIPES & FITTINGS MANUFACTURE FOR WATER SUPPLY & SEWERAGE WORKS
DOCUMENT NO: PQ/PE/NWSDB/2016/01
INSPECTION REPORT
Manufacturer : |  | St.Anthony's Industries Group (Pvt)Ltd
Factory Address : |  | 113A, Raja Mawatha, Ekala,Ja-Ela
Material : |  | HDPE Pipes as per ISO 4427 - 2007
Size : |  | PE 100 PN16 DN32x3.0MM W.T SDR11 (Blue Colour)
Dimensions:-
Sr. No. | Outer Diameter (mm) by Vernier Calliper |  |  | Ovality (mm) Max. | Wall Thickness |  | Visual Appearance | Length (Mtr.)
[5 empty] | Min. | Max. |  |  | 0.192
Standard | Min 32 | Max 32.3 |  | 1.3 | 3 | 3.4 | Shall be smooth | coil Pipes
01 | 32.3 |  |  | 32.335 | 3.15 | 3.2 | smooth
02 | 32.3 |  |  | 32.43 | 3.1 | 3.15
03 | 32.3 |  |  | 32.38 | 3.15 | 3.2
Tests:-
Sr.No. | Tests |  | Requirement |  | Results |  |  | Remark
Sample No.01
01 | Longitudinal Reversion Test Test Temp. 110 ± 2⁰C |  | ≤3% No effect on surface |  | 2.1% |  |  | satisfied
02 | Compounded Density at 23⁰C |  | ≥ 930 Kg/m³ |  | 945
03 | Elongation at Break |  | ≥ 350% |  | 594% |  |  | satisfied
04 | Thermal Stability (OIT) |  | ≥ 20 Minutes |  |  |  |  | satisfied
01 | Melt Flow Rate (MFR) at 190⁰C with 5.0 Kg Load. |  | Not more than 20% of value nominated by raw material supplier |  | 5.56% |  |  | satisfied
06 | Hydrostatic Strength 100 hrs at 20⁰C Induced Stress : 12.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
02 | Hydrostatic Strength 165 hrs at 80⁰C Induced Stress : 5.4 Mpa |  | No failure of test piece during test period. |  | No failure of test piece during test period. |  |  | satisfied
Note: Sample test only.
National Water Supply & Drainage Board
Eng. (Ms) A.S.Kaluarachchi |  |  | Eng.(Ms) Anusha Adhihetti |  |  | Eng.(Ms) G.G.S.Lekha
DGM (Development) |  |  | AGM (P&D-Doc) |  |  | CE (P&D-Doc)
Eng. (Ms) H.M.C.P.Herath |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  | (Ms) N.D.Yapa
CE (Water Reclamation) |  |  | Eng (P&D-Doc) |  |  | EA-Sp(P&D-Doc)
Bureau Veritas Lanaka (Pvt.) Ltd.
Mr. Akalanka Wickramatilake | [5 empty] | Eng. J.Karunaratne
| Manager Building & Infrastructure Services |  |  |  |  | Engineer (QA)
St. Anthony's Industries Group(Pvt.) Ltd.
Mr. Bhathiya Prabhath | [5 empty] | Mr. Amila Seneviratna
Assistant Manager (Quality Assurance) | [5 empty] | Senior Quality Assurance Officer

## Inspection 25
PRE QUALIFICATION OF PE PIPES & FITTINGS MANUFACTURE FOR WATER SUPPLY & SEWERAGE WORKS
DOCUMENT NO: PQ/PE/NWSDB/2016/01
INSPECTION REPORT
Manufacturer : |  | St.Anthony's Industries Group (Pvt)Ltd
Factory Address : |  | No.113A, Rajamawatha, Ekala, Ja-Ela
Material : |  | HDPE Pipes As per ISO 4427 - 2007
Size : |  | PE 100 PN16 DN25x2.3MM W.T SDR11 (Blue Colour)
Dimensions:-
Sr. No. | Outer Diameter (mm) by Vernier Calliper |  |  | Ovality (mm) Max. | Wall Thickness (mm) |  | Visual Appearance | Length (Mtr.)
[5 empty] | Min. | Max. |  |  | 0.15
Standard | Min 25 | Max 25.3 |  | 1.2 | 2.3 | 2.7 | Shall be smooth | coil Pipes
01 | 25.1 |  |  | 25.2125 | 2.5 | 2.7 | smooth |  |  | M/s. St. Anthony’s Industries Group (Pvt.) Ltd.,
02 | 25.2 |  |  | 25.34 | 2.45 | 2.6 |  |  |  | ,
03 | 25.3 |  |  | 25.28 | 2.45 | 2.6
Tests:-
Sr.No. | Tests |  | Requirement |  | Results |  |  | Remark
Sample No.01
01 | Longitudinal Reversion Test Test Temp. 110 ± 2⁰C |  | ≤3% No effect on surface |  | 1.9% |  |  | satsfied
02 | Compounded Density at 23⁰C |  | ≥ 930 Kg/m³ |  | 945 |  |  | satsfied
03 | Elongation at Break |  | ≥ 350% |  | 614% |  |  | satisfied
04 | Thermal Stability (OIT) |  | ≥ 20 Minutes |  |  |  |  | satisfied
05 | Melt Flow Rate (MFR) at 190⁰C with 5.0 Kg Load. |  | Not more than 20% of value nominated by raw material supplier |  |  |  |  | satisfied
06 | Hydrostatic Strength 100 hrs at 20⁰C Induced Stress : 12.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
07 | Hydrostatic Strength 165 hrs at 80⁰C Induced Stress : 5.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
Note: Sample test only.
National Water Supply & Drainage Board
Eng. (Ms) A.S.Kaluarachchi |  |  | Eng.(Ms) Anusha Adhihetti |  |  | Eng.(Ms) G.G.S.Lekha
DGM (Development) |  |  | AGM (P&D-Doc) |  |  | CE(P&D-Doc)
Eng. (Ms) H.M.C.P.Herath |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  | (Ms) N.D.Yapa
CE(Water Reclamation) |  |  | Eng(P&D-Doc) |  |  | EA-Sp (P&D-Doc)
Bureau Veritas Lanaka (Pvt.) Ltd.
Mr. Akalanka Wickramatilake | [5 empty] | Eng. J.Karunaratne
| Manager Building & Infrastructure Services |  |  |  |  | Engineer (QA)
St. Anthony's Industries Group(Pvt.) Ltd.
Mr. Bhathiya Prabhath | [5 empty] | Mr. Amila Seneviratna
Assistant Manager (Quality Assurance) | [5 empty] | Senior Quality Assurance Officer

## Inspection 25 (2)
PRE QUALIFICATION OF PE PIPES & FITTINGS MANUFACTURE FOR WATER SUPPLY & SEWERAGE WORKS
DOCUMENT NO: PQ/PE/NWSDB/2016/01
INSPECTION REPORT
Manufacturer : |  | St.Anthony's Industries Group (Pvt) Ltd.
Factory Address : |  | No.113A, Rajamawatha, Ekala, Ja-Ela
Material : |  | HDPE Pipes as per ISO 4427 - 2007
Size: |  | PE 100 PN16 DN25x2.3MM W.T SDR11 (Blue Colour)
Dimensions:-
Sr. No. | Outer Diameter (mm) by Vernier Calliper |  |  | Ovality (mm) Max. | Wall Thickness |  | Visual Appearance | Length (Mtr.)
[5 empty] | Min. | Max. |  |  | 0.15
Standard | Min 25 | Max 25.3 |  | 1.2 | 2.3 | 2.7 | Shall be smooth | coil Pipes
01 | 25.1 |  |  | 25.2125 | 2.5 | 2.7 | smooth |  |  | M/s. St. Anthony’s Industries Group (Pvt.) Ltd.,
02 | 25.2 |  |  | 25.34 | 2.45 | 2.6 |  |  |  | ,
03 | 25.3 |  |  | 25.28 | 2.45 | 2.6
Tests:-
Sr.No. | Tests |  | Requirement |  | Results |  |  | Remark
Sample No.01
01 | Longitudinal Reversion Test Test Temp. 110 ± 2⁰C |  | ≤3% No effect on surface |  | 1.9% |  |  | satsfied
02 | Compounded Density at 23⁰C |  | ≥ 930 Kg/m³ |  | 945 |  |  | satsfied
03 | Elongation at Break |  | ≥ 350% |  | 614% |  |  | satisfied
04 | Thermal Stability (OIT) |  | ≥ 20 Minutes |  |  |  |  | satisfied
05 | Melt Flow Rate (MFR) at 190⁰C with 5.0 Kg Load. |  | Not more than 20% of value nominated by raw material supplier |  |  |  |  | satisfied
06 | Hydrostatic Strength 100 hrs at 20⁰C Induced Stress : 12.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
01 | Hydrostatic Strength 165 hrs at 80⁰C Induced Stress : 5.4 Mpa |  | No failure of test piece during test period. |  | No failure of test piece during test period. |  |  | satisfied
Note: Sample test only.
National Water Supply & Drainage Board
Eng. (Ms) A.S.Kaluarachchi |  |  | Eng.(Ms) Anusha Adhihetti |  |  | Eng.(Ms) G.G.S.Lekha
DGM (Development) |  |  | AGM (P&D-Doc) |  |  | CE(P&D-Doc)
Eng. (Ms) H.M.C.P.Herath |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  | (Ms) N.D.Yapa
CE(Water Reclamation) |  |  | Eng(P&D-Doc) |  |  | EA-Sp(P&D-Doc)
Bureau Veritas Lanaka (Pvt.) Ltd.
Mr. Akalanka Wickramatilake | [5 empty] | Eng. J.Karunaratne
| Manager Building & Infrastructure Services |  |  |  |  | Engineer (QA)
St. Anthony's Industries Group(Pvt.) Ltd.
Mr. Bhathiya Prabhath | [5 empty] | Mr. Amila Seneviratna
Assistant Manager (Quality Assurance) | [5 empty] | Senior Quality Assurance Officer

## Inspection -20
PRE QUALIFICATION OF PE PIPES & FITTINGS MANUFACTURE FOR WATER SUPPLY & SEWERAGE WORKS
DOCUMENT NO: PQ/PE/NWSDB/2016/01
INSPECTION REPORT
Manufacturer: |  | St.Anthony's Industries Group (Pvt)Ltd
Factory Address: |  | 113A, Raja Mawatha, Ekala, Ja-Ela
Material: |  | HDPE Pipes As per ISO 4427 - 2007
Size: |  | PE 100 PN16 DN20x2.0MM W.T SDR11 (Blue Colour)
Dimensions:-
Sr. No. | Outer Diameter (mm) by Vernier Calliper |  |  | Ovality (mm) Max. | Wall Thickness (mm) |  | Visual Appearance | Length (Mtr.)
[5 empty] | Min. | Max. |  |  | 0.12
Standard | Min 20 | Max 20.3 |  | 1.2 | 2 | 2.3 | Shall be smooth | coil pipes
01 | 20.1 |  |  | 20.09 | 2.05 | 2.2 | smooth
02 | 20.1 |  |  | 20.09 | 2.05 | 2.15
03 | 20.1 |  |  | 20.15 | 2.05 | 2.15
Tests:-
Sr.No. | Tests |  | Requirement |  | Results |  |  | Remark
Sample No.01
01 | Longitudinal Reversion Test Test Temp. 110 ± 2⁰C |  | ≤3% No effect on surface |  | 2.6% |  |  | satisfied
02 | Compounded Density at 23⁰C |  | ≥ 930 Kg/m³ |  | 945 |  |  | satisfied
03 | Elongation at Break |  | ≥ 350% |  |  |  |  | satisfied
04 | Thermal Stability (OIT) |  | ≥ 20 Minutes |  |  |  |  | satisfied
05 | Melt Flow Rate (MFR) at 190⁰C with 5.0 Kg Load. |  | Not more than 20% of value nominated by raw material supplier |  |  |  |  | satisfied
06 | Hydrostatic Strength 100 hrs at 20⁰C Induced Stress : 12.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
07 | Hydrostatic Strength 165 hrs at 80⁰C Induced Stress : 5.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
Note: Sample test only.
National Water Supply & Drainage Board
Eng. (Ms) A.S.Kaluarachchi |  |  | Eng.(Ms) Anusha Adhihetti |  |  | Eng.(Ms) G.G.S.Lekha
DGM (Devaelopment) |  |  | AGM (P&D-Doc) |  |  | CE(P&D-Doc)
Eng. (Ms) H.M.C.P.Herath |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  | (Ms) N.D.Yapa
CE (Water Reclamation) |  |  | Eng (P&D-Doc) |  |  | EA-Sp (P&D-Doc)
Bureau Veritas Lanaka (Pvt.) Ltd.
Mr. Akalanka Wickramatilake | [5 empty] | Eng. J.Karunaratne
| Manager Building & Infrastructure Services |  |  |  |  | Engineer (QA)
St. Anthony's Industries Group(Pvt.) Ltd.
Mr. Bhathiya Prabhath | [5 empty] | Mr. Amila Seneviratna
Assistant Manager (Quality Assurance) | [5 empty] | Senior Quality Assurance Officer

## Inspection -20 (2)
PRE QUALIFICATION OF PE PIPES & FITTINGS MANUFACTURE FOR WATER SUPPLY & SEWERAGE WORKS
DOCUMENT NO: PQ/PE/NWSDB/2016/01
INSPECTION REPORT
Manufacturer: |  | St.Anthony's Industries Group (Pvt) Ltd.
Factory Address: |  | 113A, Raja Mawatha, Ekala, Ja-Ela
Material: |  | HDPE Pipes as per ISO 4427 - 2007
Size: |  | PE 100 PN16 DN20x2.0MM W.T SDR11 (Blue Colour)
Dimensions:-
Sr. No. | Outer Diameter (mm) by Vernier Calliper |  |  | Ovality (mm) Max. | Wall Thickness (mm) |  | Visual Appearance | Length (Mtr.)
[5 empty] | Min. | Max. |  |  | 0.12
Standard | Min 20 | Max 20.3 |  | 1.2 | 2 | 2.3 | Shall be smooth | coil pipes
01 | 20.1 |  |  | 20.09 | 2.05 | 2.2 | smooth
02 | 20.1 |  |  | 20.09 | 2.05 | 2.15
03 | 20.1 |  |  | 20.15 | 2.05 | 2.15
Tests:-
Sr.No. | Tests |  | Requirement |  | Results |  |  | Remark
Sample No.01
01 | Longitudinal Reversion Test Test Temp. 110 ± 2⁰C |  | ≤3% No effect on surface |  | 2.6% |  |  | satisfied
02 | Compounded Density at 23⁰C |  | ≥ 930 Kg/m³ |  | 945 |  |  | satisfied
03 | Elongation at Break |  | ≥ 350% |  |  |  |  | satisfied
04 | Thermal Stability (OIT) |  | ≥ 20 Minutes |  |  |  |  | satisfied
05 | Melt Flow Rate (MFR) at 190⁰C with 5.0 Kg Load. |  | Not more than 20% of value nominated by raw material supplier |  |  |  |  | satisfied
06 | Hydrostatic Strength 100 hrs at 20⁰C Induced Stress : 12.4 Mpa |  | No failure of test piece during test period. |  |  |  |  | satisfied
01 | Hydrostatic Strength 165 hrs at 80⁰C Induced Stress : 5.4 Mpa |  | No failure of test piece during test period. |  | No failure of test piece during test period. |  |  | satisfied
Note: Sample test only.
National Water Supply & Drainage Board
Eng. (Ms) A.S.Kaluarachchi |  |  | Eng.(Ms) Anusha Adhihetti |  |  | Eng.(Ms) G.G.S.Lekha
DGM (Development) |  |  | AGM (P&D-Doc) |  |  | CE(P&D-Doc)
Eng. (Ms) H.M.C.P.Herath |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  | (Ms) N.D.Yapa
CE(Water Reclamation) |  |  | Eng(P&D-Doc) |  |  | EA-Sp(P&D-Doc)
Bureau Veritas Lanaka (Pvt.) Ltd.
Mr. Akalanka Wickramatilake | [5 empty] | Eng. J.Karunaratne
| Manager Building & Infrastructure Services |  |  |  |  | Engineer (QA)
St. Anthony's Industries Group(Pvt.) Ltd.
Mr. Bhathiya Prabhath | [5 empty] | Mr. Amila Seneviratna
Assistant Manager (Quality Assurance) | [5 empty] | Senior Quality Assurance Officer

## Wall Thickness
Annex 7
PRE QUALIFICATION OF PE PIPES FOR WATER SUPPLY
Manufacturer : St.Anthony's Industries Group (Pvt) Ltd.
Wall Thickness for PE100, PN16, SDR 11 (BLUE)
| Date Tested | Nominal Diameter | Wall Thickness (ISO 4427:2007 - T1) |  | Measured Value | [5 empty] | Arithmatic mean | Average Mean Value
|  | dn | e min | e max | 1 | 2 | 3 | 4 | 5 | 6
| 28.06.2022 | 20 | 2 | 2.3 | 2.2 | 2.15 | 2.1 | 2.05 |  |  | 2.125 | 2.1133
[5 empty] | 2.15 | 2.13 | 2.05 | 2.1 |  |  | 2.1075
[5 empty] | 2.15 | 2.13 | 2.05 | 2.1 |  |  | 2.1075
|  | 25 | 2.3 | 2.7 | 2.7 | 2.6 | 2.5 | 2.52 |  |  | 2.58 | 2.5617
[5 empty] | 2.6 | 2.45 | 2.6 | 2.6 |  |  | 2.5625
[5 empty] | 2.6 | 2.6 | 2.45 | 2.52 |  |  | 2.5425
|  | 32 | 3 | 3.4 | 3.2 | 3.15 | 3.15 | 3.15 |  |  | 3.1625 | 3.1542
[5 empty] | 3.1 | 3.1 | 3.15 | 3.15 |  |  | 3.125
[5 empty] | 3.15 | 3.15 | 3.2 | 3.2 |  |  | 3.175
|  | 40 | 3.7 | 4.2 | 3.9 | 3.95 | 3.95 | 3.95 |  |  | 3.9375 | 3.8875
[5 empty] | 3.85 | 3.95 | 3.9 | 3.9 |  |  | 3.9
[5 empty] | 3.95 | 3.75 | 3.7 | 3.9 |  |  | 3.825
|  | 50 |  |  | 5 | 4.95 | 4.8 | 4.83 | 4.85 | 4.8 | 4.8717 | 4.8544
|  |  | 4.6 | 5.2 | 4.9 | 4.9 | 4.8 | 4.8 | 4.8 | 4.85 | 4.8417
[5 empty] | 4.85 | 4.9 | 4.85 | 4.85 | 4.85 | 4.8 | 4.85
|  | 63 | 5.8 | 6.5 | 6.15 | 6.1 | 6.3 | 6.15 | 6.45 | 6.45 | 6.2667 | 6.29
[5 empty] | 6.15 | 6.2 | 6.3 | 6.2 | 6.45 | 6.45 | 6.2917
[5 empty] | 6.35 | 6.3 | 6.15 | 6.32 | 6.3 | 6.45 | 6.3117
EN ISO 3126:2005
* | Required accuracy of individual result |  |  |  | 0.03 mm
* | Round Arithmatic mean Value to the nearest |  |  |  | 0.05mm
* | Recorded Temperature: |  | 32 | 0C
* | Instrument used: |  | Dial Thickness Guage
| * Certificate for Calibration of the Instrument: |  |  |  |  | Available
| *Date of Calibration of the Instrument: |  |  |  | 2022.05.08
|  | …………….. |  |  |  | ………………. |  |  |  | …………….
| Eng. (Ms) A.S.Kaluarachchi |  |  |  | Eng.(Ms) Anusha Adhihetti |  |  |  | Eng.(Ms) G.G.S.Lekha
| DGM (Development) |  |  |  | AGM (P&D-Doc) |  |  |  | CE(P&D-Doc)
|  | NWSDB |  |  |  | NWSDB |  |  |  | NWSDB
|  | ………………… |  |  |  | ……………. |  |  |  | ………….
| Eng. (Ms) H.M.C.P.Herath |  |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  |  | (Ms) N.D.Yapa
| CE(Water Reclamation) |  |  |  | Eng(P&D-Doc) |  |  |  | EA-Sp(P&D-Doc)
|  | NWSDB |  |  |  | NWSDB |  |  |  | NWSDB |  |  | Pg 2 / 2

## Ovality
Annex 8
PRE QUALIFICATION OF PE PIPES FOR WATER SUPPLY
| Manufacturer: |  | St.Anthony's Industries Group (Pvt) Ltd.
Out-of Roundness (Ovality) for PE100 PN16 SDR 11 (BLUE)
| Date Tested | Nominal Diameter | Maximum Out-of Roundness (ISO 4427:2007 - T1) |  | Measured Value | [5 empty] | Arithmatic mean | Average Mean Value
|  | dn |  |  | 1 | 2 | 3 | 4 | 5 | 6
| 28.06.2022 | 20 | 1.2 |  | 20.1 | 20.12 | 20.04 | 20.1 |  |  | 20.09 | 20.1083
[5 empty] | 20.12 | 20.1 | 20.1 | 20.04 |  |  | 20.09
[5 empty] | 20.2 | 20.1 | 20.12 | 20.16 |  |  | 20.145
|  | 25 | 1.2 |  | 25.53 | 25.1 | 25.1 | 25.12 |  |  | 25.2125 | 25.2775
[5 empty] | 25.72 | 25.2 | 25.2 | 25.24 |  |  | 25.34
[5 empty] | 25.3 | 25.28 | 25.26 | 25.28 |  |  | 25.28
|  | 32 | 1.3 |  | 32.6 | 32.18 | 32.16 | 32.4 |  |  | 32.335 | 32.3817
[5 empty] | 32.5 | 32.6 | 32.52 | 32.1 |  |  | 32.43
[5 empty] | 32.42 | 32.34 | 32.14 | 32.62 |  |  | 32.38
|  | 40 | 1.4 |  | 40.14 | 40.12 | 40.3 | 40.3 |  |  | 40.215 | 40.4817
[5 empty] | 40.5 | 40.5 | 40.68 | 40.78 |  |  | 40.615
[5 empty] | 40.78 | 40.8 | 40.52 | 40.36 |  |  | 40.615
|  | 50 | 1.4 |  | 50.4 | 50.3 | 50.24 | 50.2 | 50.3 | 50.2 | 50.2733 | 50.3133
[5 empty] | 50.1 | 50.4 | 50.42 | 50.34 | 50.42 | 50.32 | 50.3333
[5 empty] | 50.1 | 50.2 | 50.4 | 50.44 | 50.42 | 50.44 | 50.3333
|  | 63 | 1.5 |  | 63.72 | 63.28 | 63.44 | 63.38 | 63.3 | 63.22 | 63.39 | 63.3356
[5 empty] | 63.34 | 63.18 | 63.62 | 63.5 | 63.2 | 63.38 | 63.37
[5 empty] | 63.42 | 63.08 | 63.14 | 63.2 | 63.4 | 63.24 | 63.2467
EN ISO 3126:2005
* | Required accuracy of individual result |  |  |  | 0.1 mm
* | Recorded Temperature: |  | 32 | 0C
* | Instrument used: |  | Vernier Caliper
* | Certificate for Calibration of the Instrument: |  |  |  |  | Available
* | Date of Calibration of the Instrument: |  |  |  | 2022.04.08
|  | …………………. |  |  |  | …………………. |  |  |  | ……………
| Eng. (Ms) A.S.Kaluarachchi |  |  |  | Eng.(Ms) Anusha Adhihetti |  |  |  | Eng.(Ms) G.G.S.Lekha
| DGM (Development) |  |  |  | AGM (P&D-Doc) |  |  |  | CE(P&D-Doc)
|  | NWSDB |  |  |  | NWSDB |  |  |  | NWSDB
|  | ……………. |  |  |  | ……………. |  |  |  | ………….
| Eng. (Ms) H.M.C.P.Herath |  |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  |  | (Ms) N.D.Yapa
| CE(Water Reclamation) |  |  |  | Eng(P&D-Doc) |  |  |  | EA-Sp(P&D-Doc)
|  | NWSDB |  |  |  | NWSDB |  |  |  | NWSDB

## Diameter
Annex 9
PRE QUALIFICATION OF PE PIPES FOR WATER SUPPLY
Manufacturer : St.Anthony's Industries Group (Pvt.) Ltd.
Mean Outside Diameter for PE100 PN16 SDR 11 (BLUE)
| Date Tested | Nominal Diameter | Mean Outside Diameter (ISO 4427:2007 - T1) |  | Measured Value | [5 empty] | Arithmatic mean | Average mean value | Remarks
|  | dn | dem min | dem max | 1 | 2 | 3 | 4 | 5 | 6
| 28.06.2022 | 20 | 20 | 20.3 | 20.1 | 20.12 | 20.04 | 20.1 |  |  | 20.09 | 20.1083 | ok
[5 empty] | 20.12 | 20.1 | 20.1 | 20.04 |  |  | 20.09
[5 empty] | 20.2 | 20.1 | 20.12 | 20.16 |  |  | 20.145
|  | 25 | 25 | 25.3 | 25.1 | 25.1 | 25.1 | 25.12 |  |  | 25.105 | 25.1983 | ok
[5 empty] | 25.2 | 25.2 | 25.2 | 25.24 |  |  | 25.21
[5 empty] | 25.3 | 25.28 | 25.26 | 25.28 |  |  | 25.28
|  | 32 | 32 | 32.3 | 32.3 | 32.3 | 32.3 | 32.3 |  |  | 32.3 | 32.3 | ok
[5 empty] | 32.3 | 32.3 | 32.3 | 32.3 |  |  | 32.3
[5 empty] | 32.3 | 32.3 | 32.3 | 32.3 |  |  | 32.3
|  | 40 | 40 | 40.4 | 40.4 | 40.4 | 40.4 | 40.4 |  |  | 40.4 | 40.4 | ok
[5 empty] | 40.4 | 40.4 | 40.4 | 40.4 |  |  | 40.4
[5 empty] | 40.4 | 40.4 | 40.4 | 40.4 |  |  | 40.4
|  | 50 | 50 | 50.4 | 50.15 | 50.15 | 50.15 | 50.15 | 50.15 | 50.15 | 50.15 | 50.15 | ok
[5 empty] | 50.15 | 50.15 | 50.15 | 50.15 | 50.15 | 50.15 | 50.15
[5 empty] | 50.15 | 50.15 | 50.15 | 50.15 | 50.15 | 50.15 | 50.15
|  | 63 | 63 | 63.4 | 63.1 | 63.1 | 63.05 | 63.1 | 63.1 | 63.1 | 63.0917 | 63.075 | ok
[5 empty] | 63.1 | 63.02 | 63.05 | 63.1 | 63.02 | 63.1 | 63.065
[5 empty] | 63.1 | 63.03 | 63.05 | 63.1 | 63.03 | 63.1 | 63.0683
EN ISO 3126:2005
* | Required accuracy of individual result |  |  |  | 0.1 mm
* | Round Arithmatic mean Value to the nearest |  |  |  |  | 0.1mm
* | Recorded Temperature: |  |  | 32 | 0C
* | Instrument used: |  | Pi Tape | (2 Nos)
* | Certificate for Calibration of the Instrument: |  |  |  |  | Available
* | Date of Calibration of the Instrument: |  |  |  |  | 2022.05.23 and 2022.05.26
|  | ………………………. |  |  |  | …………………… |  |  |  | ……………..
| Eng. (Ms) A.S.Kaluarachchi |  |  |  | Eng.(Ms) Anusha Adhihetti |  |  |  |  | Eng.(Ms) G.G.S.Lekha
| DGM (Development) |  |  |  | AGM (P&D-Doc) |  |  |  |  | CE(P&D-Doc)
|  | NWSDB |  |  |  | NWSDB |  |  |  | NWSDB
|  | ……………….. |  |  |  | …………………. |  |  |  | …………………
| Eng. (Ms) H.M.C.P.Herath |  |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  |  |  | (Ms) N.D.Yapa
| CE(Water Reclamation) |  |  |  | Eng(P&D-Doc) |  |  |  |  | EA-Sp(P&D-Doc)
|  | NWSDB |  |  |  | NWSDB |  |  |  | NWSDB |  |  |  | Pg 2 / 2

## Density
Annex 10
PRE QUALIFICATION OF PE PIPES FOR WATER SUPPLY
Manufacturer : St.Anthony's Industries Group (Pvt.) Ltd.
Material Density Test Results for PE100 PN16 SDR 11 (BLUE) |  |  |  |  | Annex 9
|  | Requirement>0.930g/cm3 | at 230C
No | Diameter(mm) | Displayed Value for Pipes (g/cm3) | Avg . Density (g/cm3) | Remarks
1 | 20 | 0.942 |  | Calculated value =Displayed Value
|  | 0.944 | 0.94467
0.948
2 | 25 | 0.947 | 0.945 | do
0.947
0.941
3 | 32 | 0.94 | 0.945 | do
0.947
0.948
4 | 40 | 0.948 | 0.947 | do
0.941
0.952
5 | 50 | 0.949 | 0.946 | do
0.945
0.944
6 | 63 | 0.949 | 0.94833 | do
0.949
0.947
ISO 1183-1:2004
* | Test Method Used |  | :Immersion Method
* | Immersion Liquid Used |  | :Distilled Water
* | Recorded Temperature: |  | 270C
* | Instrument used: | Density Tester
* | Certificate for Calibration of the Instrument: |  | Available
* | Date of Calibration of the Instrument: |  | 2022.05….
………………………………. |  | ……………………………. |  | ………………………..
Eng. (Ms) A.S.Kaluarachchi |  | Eng.(Ms) Anusha Adhihetti |  | Eng.(Ms) G.G.S.Lekha
DGM (Development) |  | AGM (P&D-Doc) |  | CE(P&D-Doc)
NWSDB |  | NWSDB |  | NWSDB
……………………… |  | …………………….. |  | ……………………
Eng. (Ms) H.M.C.P.Herath |  | Eng. (Ms) W.A.S.C.Jayawickrama |  | (Ms) N.D.Yapa |  | Pg 2 / 2
CE(Water Reclamation) |  | Eng(P&D-Doc) |  | EA-Sp(P&D-Doc)
NWSDB |  | NWSDB |  | NWSDB

## Longutudinal Reversion
Annex 11
PRE QUALIFICATION OF PE PIPES FOR WATER SUPPLY
Manufacturer : St.Anthony's Industries Group (Pvt.) Ltd.
Longitudinal Reversion Test Results
SDR 11
No | Date | Pipe Diameter (mm) | Initial Length (mm) | Final Length (mm) | Longitudinal Reversion | Average Value | Remarks
1 | 2022.06.28 | 20 | 100 | 97.5 | 2.5 | 2.6333 | < 3% ok
|  |  | 100 | 96.8 | 3.2
|  |  | 100 | 97.8 | 2.2
|  |  | 100 | 96.5 | 3.5 | 2.8 | < 3% ok
|  |  | 100 | 97.3 | 2.7
|  |  | 100 | 97.8 | 2.2
|  |  | 100 | 96.5 | 3.5 | 2.9 | < 3% ok
|  |  | 100 | 97.3 | 2.7
|  |  | 100 | 97.5 | 2.5
2 | 2022.06.28 | 25 | 100 | 98 | 2 | 1.8667 | < 3% ok
|  |  | 100 | 97.7 | 2.3
|  |  | 100 | 98.7 | 1.3
|  |  | 100 | 97.2 | 2.8 | 2.1333 | < 3% ok
|  |  | 100 | 97.7 | 2.3
|  |  | 100 | 98.7 | 1.3
|  |  | 100 | 97.5 | 2.5 | 1.9 | < 3% ok
|  |  | 100 | 98.1 | 1.9
|  |  | 100 | 98.7 | 1.3
3 | 2022.06.28 | 32 | 100 | 97.6 | 2.4 | 2.0667 | < 3% ok
|  |  | 100 | 97.8 | 2.2
|  |  | 100 | 98.4 | 1.6
|  |  | 100 | 97.5 | 2.5 | 2.0333 | < 3% ok
|  |  | 100 | 97.8 | 2.2
|  |  | 100 | 98.6 | 1.4
|  |  | 100 | 97.6 | 2.4 | 2 | < 3% ok
|  |  | 100 | 98.3 | 1.7
|  |  | 100 | 98.1 | 1.9
4 | 2022.06.28 | 40 | 100 | 97.4 | 2.6 | 1.6667 | < 3% ok
|  |  | 100 | 98.3 | 1.7
|  |  | 100 | 99.3 | 0.7
|  |  | 100 | 97.4 | 2.6 | 1.9 | < 3% ok
|  |  | 100 | 98.1 | 1.9
|  |  | 100 | 98.8 | 1.2
|  |  | 100 | 97.4 | 2.6 | 2.3333 | < 3% ok
|  |  | 100 | 97.5 | 2.5
|  |  | 100 | 98.1 | 1.9
5 | 2022.06.28 | 50 | 100 | 97.5 | 2.5 | 2.2333 | < 3% ok
|  |  | 100 | 97.5 | 2.5
|  |  | 100 | 98.3 | 1.7
|  |  | 100 | 97.4 | 2.6 | 2.1333 | < 3% ok
|  |  | 100 | 97.9 | 2.1
|  |  | 100 | 98.3 | 1.7
|  |  | 100 | 97.4 | 2.6 | 2.1333 | < 3% ok
|  |  | 100 | 97.9 | 2.1
|  |  | 100 | 98.3 | 1.7
6 | 2022.06.28 | 63 | 100 | 97.7 | 2.3 | 1.3667 | < 3% ok
|  |  | 100 | 98.4 | 1.6
|  |  | 100 | 99.8 | 0.2
|  |  | 100 | 97.3 | 2.7 | 2.2667 | < 3% ok
|  |  | 100 | 97.6 | 2.4
|  |  | 100 | 98.3 | 1.7
|  |  | 100 | 97.5 | 2.5 | 1.6667 | < 3% ok
|  |  | 100 | 99.2 | 0.8
|  |  | 100 | 98.3 | 1.7
| ………………………………… |  | ………………………………… |  |  | …………………………………
| Eng. (Ms) A.S.Kaluarachchi |  | Eng.(Ms) Anusha Adhihetti |  |  | Eng.(Ms) G.G.S.Lekha
| DGM (Development) |  | AGM (P&D-Doc) |  |  | CE(P&D-Doc)
| NWSDB |  | NWSDB |  |  | NWSDB
| ………………………………… |  | ………………………………… |  |  | …………………………………
| Eng. (Ms) H.M.C.P.Herath |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  | (Ms) N.D.Yapa
| CE(Water Reclamation) |  | Eng(P&D-Doc) |  |  | EA-Sp(P&D-Doc)
| NWSDB |  | NWSDB |  |  | NWSDB |  | Pg 2 / 2

## Elongation at Break
Annex 12
PRE QUALIFICATION OF PE PIPES FOR WATER SUPPLY
ELONGATION AT BREAK TEST RESULTS
Manufacturer: St.Anthony's Industries Group (Pvt) Ltd.
Test Piece Type- Type 2
| PE100 PN16 SDR 11 (BLUE) |  |  |  |  | Marked Length =25 mm
No | Date | Diameter (mm) | Web width(mm) | Web Thickness(mm) | Loading Speed (mm/min) | Elongation (%) | Remarks
1 | 2022.06.28 | 20 |  |  |  |  | Not performed
2 | 2022.06.28 | 25 | 5.8 | 2.4 | 100 | 614 | >350% ok
|  |  | 5.8 | 2.4 |  | 556
|  |  | 5.8 | 2.4 |  | 617
3 | 2022.06.28 | 32 | 5.6 | 3.1 | 100 | 594 | >350% ok
|  |  | 5.6 | 3.1 |  | 617
|  |  | 5.6 | 3.1 |  | 593
4 | 2022.06.28 | 40 | 6 | 3.7 | 100 | 721 | >350% ok
|  |  | 6 | 3.7 |  | 564.66
|  |  | 6 | 3.7 |  | 610
5 | 2022.06.28 | 50 | 6 | 4.8 | 100 | 426 | >350% ok
|  |  | 6 | 4.8 |  | 419
|  |  | 6 | 4.8 |  | 530
6 | 2022.06.28 | 63 | 5.6 | 5.8 | 50 | 423 | >350% ok
|  |  | 5.6 | 5.8 |  | 542
|  |  | 5.6 | 5.8 |  | 635
ISO 4427-2:2007, ISO 6259-1:2015 and ISO 6259-3:2015
* | Method Used to prepare Test pieces |  |  | Cutting Die
* | Recorded Temperature: |  | 230C
* | Instrument used: |  | “Testometric” Tensile Testing machine
* | Certificate for Calibration of the Instrument: |  |  |  | Available
* | Date of Calibration of the Instrument: |  | 2021.01.21
| ………………………………… |  |  | ……………………………….. |  | ………………………………
Eng. (Ms) A.S.Kaluarachchi |  |  |  | Eng.(Ms) Anusha Adhihetti |  | Eng.(Ms) G.G.S.Lekha
DGM (Development) |  |  |  | AGM (P&D-Doc) |  | CE(P&D-Doc)
NWSDB |  |  |  | NWSDB |  | NWSDB
| …………………….. |  |  | ……………………. |  | ………………
Eng. (Ms) H.M.C.P.Herath |  |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  | (Ms) N.D.Yapa
CE(Water Reclamation) |  |  |  | Eng(P&D-Doc) |  | EA-Sp(P&D-Doc) |  | Pg 2 / 2
NWSDB |  |  |  | NWSDB |  | NWSDB

## Melt Mass Flow (2)
Testing of Sierra Pipes Brand PE pipes
Melt Mass Flow Rate
Particulars of Samples |  | :Samples of Sierra Pipes Brand PE Pipes (PE 100, SDR 11) -Sierra Industries (PVT)Ltd.
Sample No. | Brand | Sample Description
Sample No.1 | Sierra Pipes | 20 mm
Sample No.2
Test Performed: |  | Tests were carried out accordance with SLS 1498:2015 standards
Results
Sample No. | Tested Property | Unit | Requirement | Test Results
|  |  |  | Test Piece -1 | Test Piece -2 | Test Piece -3
Sample No.1 | Melt Mass Flow rate | % | Change of Value as measured on the pipe, relative to the value measured on the compound by + 20 % |  |  |  |  | #DIV/0!
Sample No.2
#DIV/0!
Eng. H.K. Primal K. Jinadasa |  |  | Eng. (Ms.) K.P.P. Dharmasena |  | Eng. (Ms.) G.G.S. Lekha
PD (Anamaduwa) |  |  | AGM (P&D-Doc) |  | CE(P&D-Doc)
NWS & DB |  |  | NWS & DB |  | NWS & DB
Eng. H.M.C.P.Herath |  |  | Eng. J.N.C.G. Jayasinghe |  | Eng. W.A.S.C.Jayawickrama
CE(WR) |  |  | Eng. (P&D-N,C) |  | Eng(P&D-Doc) |  |  |  | Pg 2 / 2
NWS & DB |  |  | NWS & DB |  | NWS & DB

## Melt Mass Flow
Melt Mass Flow Rate Test Results
Manufacturer: |  | St.Anthony's Industries Group (PVT)Ltd.
SDR 11
Time | 10min |  |  | Temperature-190 |  | 0C | Date:06.07.2022
Sample No. | Material | Measured weight of the Extrude(g) |  |  | Melt Mas Flow rate % |  |  | Requirement
|  | Test Piece 1 | Test Piece 2 | Test Piece 3 | Test Piece 1 | Test Piece 2 | Test Piece 3
1 | Raw Material | 0.3 | 0.29 | 0.31 |  |  |  | Change of MFR by Processing +20 % (value as measured on the pipe, relative to the value measured on the compound (<20))
|  | 0.3 |  |  | - | - | -
2 | Pipe Material-50mm | 0.3 | 0.33 | 0.33 | 0 | 10 | 10
3 | Pipe Material-32mm | 0.32 | 0.32 | 0.31 | 6.6667 | 6.6667 | 3.3333
Eng. (Ms) A.S.Kaluarachchi |  |  | Eng.(Ms) Anusha Adhihetti |  |  | Eng.(Ms) G.G.S.Lekha
DGM (Development) |  |  | AGM (P&D-Doc) |  |  | CE(P&D-Doc)
NWSDB |  |  | NWSDB |  |  | NWSDB
Eng. (Ms) H.M.C.P.Herath |  |  | Eng. (Ms) W.A.S.C.Jayawickrama |  |  | (Ms) N.D.Yapa
CE(Water Reclamation) |  |  | Eng(P&D-Doc) |  |  | EA-Sp(P&D-Doc)
NWSDB |  |  | NWSDB |  |  |  | NWSDB
Mr. Akalanka Wickramatilake |  |  | Eng. J.Karunaratne
Manager Building & Infrastructure Services |  |  | Engineer (QA)
Bureau Veritas Lanaka( Pvt.) Ltd. |  |  | Bureau Veritas Lanaka (Pvt.) Ltd.

## Sheet1
Testing of Sierra Pipes Brand PE pipes
Melt Mass Flow Rate
Particulars of Samples |  | :Samples of Sierra Pipes Brand PE Pipes (PE 100, SDR 17) -Sierra Industries (PVT)Ltd.
Sample No. | Brand | Sample Description
Sample No.1 | Sierra Pipes | 32mm
Sample No.2
Test Performed: | Tests were carried out accordance with SLS 1498:2015 standards
Results
Sample No. | Tested Property | Unit | Requirement | Test Results
|  |  |  | Test Piece -1 | Test Piece -2 | Test Piece -3
Sample No.1 | Melt Mass Flow rate | % | Change of Value as measured on the pipe, relative to the value measured on the compound by + 20 % |  |  |  |  | #DIV/0!
Sample No.2
#DIV/0!
Eng. H.K. Primal K. Jinadasa |  |  | Eng. (Ms.) K.P.P. Dharmasena |  | Eng. (Ms.) G.G.S. Lekha
PD (Anamaduwa) |  |  | AGM (P&D-Doc) |  | CE(P&D-Doc)
NWS & DB |  |  | NWS & DB |  | NWS & DB
Eng. H.M.C.P.Herath |  |  | Eng. J.N.C.G. Jayasinghe |  | Eng. W.A.S.C.Jayawickrama
CE(WR) |  |  | Eng. (P&D-N,C) |  | Eng(P&D-Doc) |  |  |  | Pg 2 / 2
NWS & DB |  |  | NWS & DB |  | NWS & DB