SPECIFICATIONS FOR HIGH DENSITY POLYETHYLENE (HDPE) PIPES, FITTINGS, SPECIALS & ACCESSORIES FOR

DRAINAGE & SEWERAGE APPLICATIONS

Revised on 29.01.2024

ANNEX A

Table 2 – Characteristics of the PE compound as granules

| Characteristics | Requirements a | Test parameters |  | Test method |
| --- | --- | --- | --- | --- |
|  |  | Parameter | Value |  |
| Compound density | ≥ 930 kg/m 3 | Test temperature Number of Samples | 230C shall conform to EN ISO 1183-1 and EN ISO 1183-2 | EN ISO 1183-1 and EN ISO 1183-2 |
| Carbon black content (black compound) | (2 to 2.5)% by mass | Shall conform to ISO 6964 |  | ISO 6964 |
| Carbon black dispersion (black compound) | Grade ≤ 3 Rating of dispersion A1, A2, A3 or B | Shall conform to ISO 18553c |  | ISO 18553 |
| Pigment dispersion (blue compound) | Grade ≤ 3 Rating of dispersion A1, A2, A3 or B | Shall conform to ISO 18553c |  | ISO 18553 |
| Water content b | ≤ 300 mg/kg | Number of test pieces d | 1 | EN ISO 15512 |
| Volatile content | ≤ 350 mg/kg | Number of test pieces d | 1 | EN 12099 |
| Oxidation induction time | ≥ 20 min | Test temperature Number of test pieces d Test atmosphere Sample weight | 200 0C e 3 Oxygen (15+/-2) mg | ISO 11357-6 |
| Melt mass-flow rate (MFR) for PE 100 | (0.2 to 1.4) g/10 min Maximum deviation of ±20% of the nominated valuef | Load Test temperature Time Number of test pieces d | 5 kg 1900C 10 min shall confirm to EN ISO 1133 | EN ISO 1133 |
| a Conformity to these requirements shall be proved by the compound manufacture. |  |  |  |  |
| b Only applicable if the measured volatile content is not in conformity with its specified requirement. In case of dispute the requirement for water content shall apply. An alternative test method ISO 760:1978 [5] may be used. The requirement applies to the compound producer at the stage of manufacturing and to the compound user at the stage of processing (if the water content exceeds the limit, drying is required prior to use). |  |  |  |  |
| c In case of dispute the test pieces for carbon black dispersion and pigment dispersion shall be prepared by the compression method. |  |  |  |  |
| d The given number of test pieces indicates the quantity required to establish a value for the characteristic described in the table. The number of test pieces required for factory production control and process control should be listed in the manufacturer’s quality plan. For guidance see CEN/TS 12201-7 [2]. |  |  |  |  |
| e Test may be carried out as an indirect test at 210oC or 220oC, providing that a clear correlation has been established. In the case of dispute the test temperature shall be 200oC |  |  |  |  |
| f Nominated value given by the compound producer. |  |  |  |  |

Revised on 29.01.2024