Ref. No.: NWSDB/SBD/S&I/Sewage Pump (above 30kW)/FC/Ver 2

Revised on 17-06-2024

GOVERNMENT OF THE DEMOCRATIC SOCIALIST REPUBLIC

# OF SRI LANKA

## MINISTRY OF …………………………………..

# NATIONAL WATER SUPPLY AND DRAINAGE BOARD

SUPPLY AND INSTALLATION OF SEWAGE PUMPING SETS

AND ACCESSORIES

(Above 30kW)

CONTRACT No.: …………………………………..

Revised on 17-06-2024

NATIONAL WATER SUPPLY AND DRAINAGE BOARD

GALLE ROAD,

RATMALANA.

SRI LANKA

……………………

(MONTH & YEAR)

#### DOCUMENT ISSUANCE CERTIFICATE

(To be filled at the time of issue by the authorized issuing officer)

1.	STANDARD DOCUMENT REFERENCE NUMBER: NWSDB/SBD/S&I/Sewage Pump/FC/Ver2

2.	CONTRACT NUMBER 	:   ………………….…………..………………………..

3.	a)	ISSUED TO		:	………..........................……...............................

b)	ADDRESS		:	………….................................……....................

c)	TELEPHONE NUMBER	:	....……...............................…..................

d)	FACSIMILE NUMBER	:	………………………………..………..

4.        a)        NON REFUNDABLE

TENDER FEE	:	Rs. .................. RECEIVED/NOT RECEIVED

IN CASH/BANK DRAFT

b)	RECEIPT/BANK DRAFT NUMBER	:	.....................……............

5.	NUMBER OF COPIES ISSUED	:	..................…….…....................…...........

6.	NUMBER OF CANCELLED COPIES ISSUED	:	…….....................……….

7.	CANCELLED COPY FEE	:       Rs...............…….... RECEIVED/NOT RECEIVED

(IN CASH/BANK DRAFT)

8	BUSINESS REGISTRATION NUMBER	: ..........................………..........................

9.	a)	ISSUING OFFICER		:	................................................…………..

b)	DESIGNATION		:	....................................................………..

c)	SIGNATURE			:	..................................................…………

10.	PLACE OF ISSUE			:	........................................................……..

11.	SEAL		:	………………..…………………………………………………

12.	DATE		:	............................ 	TIME 	: …................................................

### Table of Contents

SECTION							PAGE  NUMBER

Revised on 17-06-2024

|  |  | From To |
| --- | --- | --- |
|  | Document Issuance Certificate Table of contents | (i) (ii) (iii) |
|  | Checklist of Submissions | (iv) |
| 1. 2. | Invitation for Bids Instructions to Bidders Conditions of contract | (v) 1 – 1 1 - 26 2 - 1 2 - 47 |
| 3. | Form of Bid | 3 - 1 3 - 2 |
| 4. | Bidding Data | 4 - 1 4 - 5 |
| 5. | Contract Data |  |
|  | * General | 5 - 1 5 - 4 |
|  | * Delivery Schedule | 5 - 5 |
|  | * Payment Schedule | 5 - 6 |
| 6. | Specifications | 6a - 1 6f - 17 |
| 7. 8. | Schedule of Particulars Deviation from Specifications | 7a- 1 7f – 3 8 – 1 |
| ## 0 | Bills of Quantities | 10-1 10 – 11 |

| ## SECTION |  | PAGE NUMBER |
| --- | --- | --- |
| ## 11 | Specimen Forms - Bid Security - Contract Agreement - Performance Guarantee - Letter of Acceptance - Retention Money Guarantee | 11 - 1 11- 2 - 11 - 5 11 -6 11 - 7 11 - 8 11 - 9 |
| ## 12 | Appendices |  |
|  | Appendix 1A– Detail of Similar Supplies Completed within The last five years and ongoing. Appendix 1B – Details of Similar Installations Completed Within the last five years and ongoing. Appendix 2 – Schedule of Technical Persons & Facilities Appendix 3 –. Financial Statement Appendix 3A – Authorization for Bank references Appendix 4.- Confirmation of capability of Production and Supply according to delivery schedule Appendix 5 - Manufacturer’s Authorization to sign the Contract. Appendix 6 - Schedule of Plant and Equipment Proposed for Pumps, Installations Appendix 7 - Bidder’s authorizations to sign the contract Appendix 8 - TOR for Independent Inspection Agency Inspection of Pump Motor Assemblies Appendix 9 - Manufacturer’s awareness of the TOR for Independent Inspection Agency and checklist for Pre-Shipment Inspections Appendix 10 - Manufacturer’s Warranty for the goods supplied under the contract Appendix 11 - Pre-Shipment Inspection of Pump and Motor Assemblies by Team of NWSDB Engineers Appendix 12 - Guidelines for the acceptance of Pump and Motor Assemblies at NWSDB site by the Inspection Team. Appendix 13 – Affidavit by the Bidder Appendix 14 - Entitled allowances on foreign travels & related expenses | 12 -1 12– 2 12 - 3 12 - 4 12 – 5 12 – 6 12 – 7 12 -8 - 12–10 12 – 11 12 –12 12 - 13 12 –14 12 –15 12 – 16 12 – 17 12 – 18 12 – 19 12 – 20 12 – 21 |

# CHECKLIST OF SUBMISSIONS

# CHECKLIST OF SUBMISSIONS

*	Note: Please mark ’Y’ in the cages under the ‘Remarks’ column if submissions are made.

‘N’ or ‘N/A’ should be marked for cases of ‘No submissions’ and ‘Not applicable’ respectively.

Revised on 17-06-2024

|  |  | ## Reference Instructions to Bidders |  | ## Remarks * |
| --- | --- | --- | --- | --- |
| (a) | Documentary evidence to establish eligibility of bidder. | Page No 1 -5, 1- 6 | Clause No. 4 .1 |  |
| (b) | Certified copy of business registration. | Page No. 1 - 6 | Clause No. 4.1 (vii) |  |
| (c) | The Bidder’s technical and production capability necessary to perform the Contract. | Page No. 1 - 6 | Clause No 4.2 (iii) |  |
| (d) | Documentary evidence to establish qualifications for the performance of the Contract. | Page No. 1 - 6, 1- 7 | Clause No. 4.2 |  |
| (e) | The agreement of the manufacturer or producer to confirm that the supply will be made in accordance with the Delivery Schedule. | Page No. 1 - 7 | Clause No. 4.2 (v) |  |
| (f) | In the case of a bidder offering to supply Goods under the Contract which the bidder does not manufacture or otherwise produce, authorisation by the manufacturer or producer of Goods as his accredited agent. | Page No. 1 - 7 | Clause No. 4.2 (vi) |  |
| (g) | Documentary evidence to establish that goods and related services offered are from an eligible source and origin. | Page No. 1 - 7 | Clause No. 5 |  |
| (h) | Duly completed all sections of Bidding Documents. (Bidder shall fill the Schedule of Particulars, BOQ etc., indicating any deviations to specifications under the corresponding schedule of particulars) | Page No. 1 -7, 1-8, 1 - 10 | Clause No. 11.1 (a) |  |
| (i) | Subsequent Addendum/Addenda (if any) | Page No. 1 - 10 | Clause No. 11.1 (h) |  |
| (j) | Product Conformity Certificates and Quality Management Certificates for items offered. | Page No. 1- 10 | Clause No. 11.1(k) |  |
| (k) | Proof of Authorization. | Page No. 1 - 10 | Clause No. 11.1 (m) |  |
| (l) | Other Documents comprising the Bid. | Page No. 1 - 10 | Clause No. 11.1 |  |
| (m) | Certified Copy of the VAT Registration Certificate. | Page No. 1 - 12 | Clause No. 14.4 |  |
| (n) | Bid Security. | Page No. 1 - 15 | Clause No. 20 |  |
| (o) | Certificates of registration of the contract with the registrar of public contracts as per the Act No. 3 of 1987. (If required) | Page No. 1-26 | Clause No. 47 |  |
|  | Any other document as given below: | Page No. 1 – 11 | Clause No. 11.1 (p) |  |

- INVITATION FOR BIDS

MINISTRY OF …………………………………………………………………………..

NATIONAL WATER SUPPLY AND DRAINAGE BOARD

- INVITATION FOR BIDS

SUPPLY AND INSTALLATION OF SEWAGE PUMPING

SETS AND ACCESSORIES

- FOR……………………………………….SEWERAGE SCHEME

- CONTRACT No.: ………………………………………………

- The Chairman, Cabinet Appointed Procurement Committee, Ministry of  …………… ……………………………………………………..,   No. 35, “Lakdiya Medura”, New Parliament Road, Pelawatta, Battaramulla, Sri Lanka will receive sealed bids for the supply and Installation of …………………………………………………..for …………………..Water Supply Scheme   up to closing of bids at ……………. hours on …………. .

- Bidding documents are available at the office of the Assistant General Manager (Tenders and Contracts), National Water Supply & Drainage Board (NWSDB), Galle Road, Ratmalana between 09:00 hours to 15:00 hours on normal working days up to  ...................................., upon payment of a non refundable fee of Rs. ………………... plus applicable VAT.

- Bidding Documents may be inspected free of charge at the office of the Assistant General Manager (Tenders and Contracts), NWSDB, Galle Road, Ratmalana.

- Bidding Documents will be issued only to those who are manufacturers or their local Accredited Agents for supply of Sewage Pumping Sets upon production of a letter of request for documents on a business letterhead together with Certificate of Registration of the Contract as per the Act No. 3 of 1987 with the Registrar of Public Contract and the proof or manufacturer or their local accredited agent.  Joint Ventures are not acceptable.

5.	To be eligible for contract award, the successful bidder shall not have been blacklisted.

6.	Alternative bids shall not be accepted.

7.	Sealed bids may be either dispatched by registered post or hand delivered to the Procurement Division, Ministry of  ……………………………………………………, No. 35, “Lakdiya Medura”, New Parliament Road, Pelawatta, Battaramulla, Sri Lanka to receive on or before the closing time.  Late Bids will be rejected.

8.	All Bids shall be accompanied by a bid security of Rupees…………………and the bid security shall be valid upto………………( Specify the Date).

9.	Bids will be opened immediately after the closing of bids, at the office of the Procurement Division, Ministry of  ……………………………………………………, No. 35, “Lakdiya Medura”, New Parliament Road, Pelawatta, Battaramulla, Sri Lanka. Bidders or their authorised representatives may be present at the opening of bids.

10. For further details, please contact the Assistant General Manager (Tenders and Contracts), NWSDB, Galle Road,  Ratmalana  on telephone  number  94 - 11-2605328  or 94 -11-2638999, Extension 1750 or  facsimile number   94 -11-2635885.

- Chairman,

- NATIONAL WATER SUPPLY AND DRAINAGE BOARD

Revised on 22-03-2023

MINISTRY OF …………………………………………………………………………………….. NATIONAL WATER SUPPLY AND DRAINAGE BOARD

- INVITATION FOR BIDS

SUPPLY AND INSTALLATION OF SEWAGE PUMPING

SETS AND ACCESSORIES

SEWERAGE

…………………………. SEWERAGE SCHEME

- CONTRACT No.: ………………………………………………

- ----------------------------------------------------------------------------------------------------------------

- 1.	The Chairman,  Ministry  Procurement Committee, Ministry of  …………………... …………………………………….., No. 35, “Lakdiya Medura”, New Parliament Road, Pelawatta, Battaramulla, Sri Lanka will receive sealed bids for the supply and Installation of…………..…………………………………………………….….Water Supply Scheme up to closing of bids at ……………. hours on …………. .

2.	Bidding documents are available at the office of the Assistant General Manager (Tenders and Contracts), National Water Supply & Drainage Board (NWSDB), Galle Road, Ratmalana, Sri Lanka between 09:00 hours to 15:00 hours on normal working days up to  ...................................., upon payment of a non refundable fee of Rs. ………………plus applicable VAT.

3.	Bidding Documents may be inspected free of charge at the office of the Assistant General Manager (Tenders and Contracts), NWSDB, Galle Road, Ratmalana.

4.	Bidding Documents will be issued only to those who are manufacturers or their local accredited agents for supply of Sewage Pumping Sets upon production of a letter of request for documents on a business letterhead together with Certificate of Registration of the Contract as per the Act No. 3 of 1987 with the Registrar of Public Contract and the proof or manufacturer or their local accredited agent. Joint Ventures are not acceptable.

5.		To be eligible for contract award, the successful bidder shall not have been blacklisted.

6.	Alternative bids shall not be accepted.

7.	Sealed bids may be either dispatched by registered post or hand delivered to the Procurement Division, Ministry of  ……………………………………………………, No. 35, “Lakdiya Medura”, New Parliament Road, Pelawatta, Battaramulla, Sri Lanka to receive on or before the closing time.  Late Bids will be rejected.

8.	All Bids shall be accompanied by a bid security of Rupees…………………and the bid security shall be valid upto………………(Specify the Date).

9.	Bids will be opened immediately after the closing of bids, at the office of the Procurement Division, Ministry of ……………………………………………………., No. 35, “Lakdiya Medura”, New Parliament Road, Pelawatta, Battaramulla, Sri Lanka. Bidders or their authorised representatives may be present at the opening of bids.

10.	For further details, please contact the Assistant General Manager (Tenders and Contracts), NWSDB, Galle Road, Ratmalana on  telephone  number  94 -11-2605328 or  94 -11-2638999 Extension 1750   or  facsimile number 94 -11-2635885.

- Chairman,

NATIONAL WATER SUPPLY AND DRAINAGE BOARD

Revised on 22-03-2023

MINISTRY OF ……………………………………………………………………………

NATIONAL WATER SUPPLY AND DRAINAGE BOARD

- INVITATION FOR BIDS

SUPPLY AND INSTALLATION OF SEWAGE PUMPING

SETS AND ACCESSORIES

……………………………………….. SEWERAGE SCHEME

- CONTRACT No.: ………………………………………………

- ------------------------------------------------------------------------------------------------------------

1.	The Chairman, Department Procurement Committee, National Water Supply and Drainage Board (NWSDB), Galle Road, Ratmalana, Sri Lanka on behalf of  NWSDB  will receive sealed bids for the supply and Installation of  ………………………………for …………..Water Supply Scheme up to closing of bids at ……………. hours on …………. .

2.	Bidding documents available at the office of the Assistant General Manager (Tenders and Contracts), National Water Supply & Drainage Board (NWSDB), Galle Road, Ratmalana, Sri Lanka between 09:00 hours to 15:00 hours on normal working days up to  ...................................., upon payment of a non refundable fee of Rs. ………………plus applicable VAT.

3.	Bidding Documents may be inspected free of charge at the office of the Assistant General Manager (Tenders and Contracts), NWSDB, Galle Road, Ratmalana, Sri Lanka.

4          Bidding Documents will be issued only to those who are manufacturers or their local

accredited agents for supply of Sewage Pumping Sets upon production of a letter of request for documents on a business letterhead together with Certificate of Registration of the Contract as per the Act No. 3 of 1987 with the Registrar of Public Contract and the proof or manufacturer or their local accredited agent.  Joint Ventures are not acceptable.

5.		To be eligible for contract award, the successful bidder shall not have been blacklisted.

6.	Alternative bids shall not be accepted.

7.	Sealed bids may be either dispatched by registered post or hand delivered to the Assistant General Manager (Tenders and Contracts), NWSDB, Galle Road, Ratmalana, Sri Lanka to receive on or before the closing time.  Late Bids will be rejected.

8.	All Bids shall be accompanied by a bid security of Rupees…………………and the bid security shall be valid upto………………(Specify the Date).

9.	Bids will be opened immediately after the closing of Bids, at the office of the Assistant General Manager (Tenders and Contracts), NWSDB, Galle Road, Ratmalana, Sri Lanka. Bidders or their authorised representatives may be present at the opening of bids.

10.	For further details, please contact the Assistant General Manager (Tenders Contracts), NWSDB, Galle Road, Ratmalana, Sri Lanka on telephone number  94-11-2605328 or 94-11-2638999 Extension 1750  or   facsimile  number 94 -11-2635885.

- Chairman,

NATIONAL WATER SUPPLY AND DRAINAGE BOARD

Revised on 22-03-2023

3. FORM OF BID

THE GOVERNMENT OF THE DEMOCRATIC SOCIALIST REPUBLIC OF SRI LANKA

MINISTRY OF ………………………………………………………………..

NATIONAL WATER SUPPLY AND DRAINAGE BOARD

SUPPLY AND INSTALLATION OF SEWAGE PUMPING

SETS AND ACCESSORIES

……………………… SEWERAGE SCHEME

CONTRACT No.: …………………………….

FORM OF BID

The Chairman,

Cabinet Appointed Procurement Committee,

Ministry of  ……………………………………………….,

No. 35, “Lakdiya Medura”

New Parliament Road,

Pelawatta

Battaramulla

I/We, the undersigned, having authority to sign this Bid and having read and fully acquainted myself/ourselves with the contents of the Information and Instructions to Bidders and Terms and Conditions of Tender pertaining to the above bid, along with Bills ......... thereto, do hereby undertake to supply the Goods and Services referred to therein, in accordance with the aforesaid Instructions, Terms and Conditions for a total Bid price of Rupees …………… ……................................................…………………………………………………………….. …………………………… (in words) (LKR..................………………........... …………..) (excluding VAT) The make up of the aforesaid total Bid Price is given in the accompanying Bills of Quantities.

I/We confirm that this offer shall be open for acceptance until as given in the Bidding Data and that it will not be withdrawn or revoked prior to that date.

I/We attach hereto the following documents as part of my/our Bid.

- Duly completed sections 1 to 12 of Bidding Documents

- Documentary evidence to establish eligibility of bid.

- Documentary evidence to establish that goods and related services are offered from an eligible source and origin.

- Documentary evidence to establish eligibility of goods offered.

- Bid Security

- Documentary evidence to establish qualifications for the performance of the Contract.

- Contract Data

- Bidding Data

Any other document.

Revised on 10-11-2020

I/We declare that the photostat copies of documents and certificates submitted as part of my/our Bid are true copies of such documents and certificates. Also in case of ISO 9001:2015 certificate(s), I/we confirm that I/we have verified that the certificate issuing authority has accreditation to issue same and materials offered conform to the ISO series certificates and the specified product standard certificates.

I/We further agree to the right of the Board to debar me/us from participating in its future bids in the event that my/our submitted copies or documents are found to be forged or tampered with.

I/We understand that you are not bound to accept the lowest bid and that you reserve the right to reject any or all bids or to accept any part of a bid without assigning any reasons thereto.

I/We undertake to adhere to the Delivery Schedule given in Contract Data.

My/Our Bank Reference is as follows: ................................................................................

...............................................................................................................................................

Signature of Bidder		: .............................................................................................

Name of Bidder		: .............................................................................................

Address			: .............................................................................................

Telephone Number		: .............................................................................................

Facsimile Number		: .............................................................................................

Date				: ............................................................................................

## Witnesses

1. Name			:  ...........................................................................................

Capacity	:  .............................................................................................

Address			: .............................................................................................

Signature			:  …………………………………………………………...

2. Name			:  ...........................................................................................

Capacity	:  .............................................................................................

Address			: .............................................................................................

Signature			:.............................................................................................

THE GOVERNMENT OF THE DEMOCRATIC SOCIALIST REPUBLIC OF SRI LANKA

MINISTRY OF …………………………………………………………………

NATIONAL WATER SUPPLY AND DRAINAGE BOARD

SUPPLY AND INSTALLATION OF SEWAGE	 PUMPING

SETS AND ACCESSORIES

…………………………. SEWERAGE SCHEME

CONTRACT No.: …………………………….

FORM OF BID

The Chairman,

Ministry Procurement Committee,

Ministry of  ……………………………………………..,

No. 35, “Lakdiya Medura”

New Parliament Road,

Pelawatta

Battaramulla

I/We, the undersigned, having authority to sign this Bid and having read and fully acquainted myself/ourselves with the contents of the Information and Instructions to Bidders and Terms and Conditions of Tender pertaining to the above Bid, along with Bills ......... thereto, do hereby undertake to supply the Goods and Services referred to therein, in accordance with the aforesaid Instructions, Terms and Conditions for a total Bid price of Rupees ........................... .....................……………………..……….………………………………….……...(in words) (LKR.............…………......... …………..) (Excluding VAT) The make up of the aforesaid total Bid Price is given in the accompanying Bills of Quantities.

I/We confirm that this offer shall be open for acceptance until as given in the Bidding Data and that it will not be withdrawn or revoked prior to that date.

I/We attach hereto the following documents as part of my/our Bid.

- Duly completed sections 1 to 12 of Bidding Documents.

- Documentary evidence to establish eligibility of bid.

- Documentary evidence to establish that goods and related services are offered from an eligible source and origin.

- Documentary evidence to establish eligibility of goods offered.

- Bid Security.

- Documentary evidence to establish qualifications for the performance of the Contract.

- Contract Data.

- Bidding Data.

Any other document.

Revised on 10-11-2020

I/We declare that the Photostat copies of documents and certificates submitted as part of my/our Bid are true copies of such documents and certificates. Also in case of ISO 9001:  2015 certificate(s), I/we confirm that I/we have verified that the certificate issuing authority has accreditation to issue same and materials offered conform to the ISO series certificates and the specified product standard certificates.

I/We further agree to the right of the Board to debar me/us from participating in its future bids in the event that my/our submitted copies or documents are found to be forged or tampered with.

I/We understand that you are not bound to accept the lowest bid and that you reserve the right to reject any or all bids or to accept any part of a bid without assigning any reasons thereto.

I/We undertake to adhere to the Delivery Schedule given in Contract Data.

My/Our Bank Reference is as follows: ................................................................................

.................................................................................................................................................

Signature of Bidder		: .............................................................................................

Name of Bidder		: .............................................................................................

Address			: .............................................................................................

Telephone Number		: .............................................................................................

Facsimile Number		: ............................................................................................

Date				: .............................................................................................

## Witnesses

1. Name			:  ...........................................................................................

Capacity	:  .............................................................................................

Address			: .............................................................................................

Signature			:  …………………………………………………………...

2. Name			:  ...........................................................................................

Capacity	:  .............................................................................................

Address			: .............................................................................................

Signature			:.............................................................................................

THE GOVERNMENT OF THE DEMOCRATIC SOCIALIST REPUBLIC OF SRI LANKA

MINISTRY OF ………………………………………………………………………

NATIONAL WATER SUPPLY AND DRAINAGE BOARD

SUPPLY AND INSTALLATION OF SEWAGE PUMPING

SETS AND ACCESSORIES

………………………….. SEWERAGE SCHEME

CONTRACT No.: …………………………….

FORM OF BID

The Chairman,

Department  Procurement Committee,

National  Water  Supply  and  Drainage  Board,

Galle Road,

Ratmalana.

I/We, the undersigned, having authority to sign this Bid and having read and fully acquainted myself/ourselves with the contents of the Information and Instructions to Bidders and Terms and Conditions of Tender pertaining to the above bid, along with Bills ......... thereto, do hereby undertake to supply the Goods and Services referred to therein, in accordance with the aforesaid Instructions, Terms and Conditions for a total Bid price of Rupees ……………....... ………………….....................……………….…..………………..……………..… (in words) (LKR.............…………………….................…………..) (excluding VAT). The make up of the aforesaid total Bid Price is given in the accompanying Bills of Quantities.

I/We confirm that this offer shall be open for acceptance until as given in the Bidding Data and that it will not be withdrawn or revoked prior to that date.

I/We attach hereto the following documents as part of my/our Bid.

- Duly completed sections 1 to 12 of Bidding Documents.

- Documentary evidence to establish eligibility of bid.

- Documentary evidence to establish that goods and related services are offered from an eligible source and origin.

- Documentary evidence to establish eligibility of goods offered.

- Bid Security.

- Documentary evidence to establish qualifications for the performance of the Contract.

- Contract Data.

- Bidding Data.

- Any other document.

Revised on 10-11-2020

I/We declare that the photostat copies of documents and certificates submitted as part of my/our Bid are true copies of such documents and certificates. Also in case of ISO 9001 :  2015 certificate(s), I/we confirm that I/we have verified that the certificate issuing authority has accreditation to issue same and materials offered conform to the ISO series certificates and the specified product standard certificates.

I/We further agree to the right of the Board to debar me/us from participating in its future bids in the event that my/our submitted copies or documents are found to be forged or tampered with.

I/We understand that you are not bound to accept the lowest bid and that you reserve the right to reject any or all bids or to accept any part of a bid without assigning any reasons thereto.

I/We undertake to adhere to the Delivery Schedule given in Contract Data.

My/Our Bank Reference is as follows……………………………………………………

……………………………………………………………………………………………….

Signature of Bidder		: .............................................................................................

Name of Bidder		: .............................................................................................

Address			: .............................................................................................

Telephone Number		: .............................................................................................

Facsimile Number		: .............................................................................................

Date				: .............................................................................................

## Witnesses

1. Name			:  ...........................................................................................

Capacity	:  .............................................................................................

Address			: .............................................................................................

Signature			:  …………………………………………………………...

2. Name			:  ...........................................................................................

Capacity	:  .............................................................................................

Address			: .............................................................................................

Signature			:.........................................................................................

## 4.   BIDDING DATA

The Bidding Data is a part of Instructions to Bidders and should be read in conjunction with the Instructions to Bidders.

If there is a discrepancy found in the Instructions to Bidders and the Bidding Data, the Content in the Bidding Data shall supersede the Content in the Instructions to Bidders.

(Note: What is typed in italic letters are guide lines to prepare the Bidding Data and they shall be removed after preparation of the Bidding Data.)

| Bidding Data (Please note that the clause numbers given here under are that of Instructions to Bidder) The following specific data for the goods and related services to be procured shall complement, supplement, or amend the provisions in the Instructions to Bidders (ITB). Whenever there is a conflict, the provisions herein shall prevail over those in ITB. |  |
| --- | --- |
| ITB Clause Reference | A. General |
| 1.1 | The Purchaser / Employer is Name: National Water Supply and Drainage Board Address: Galle Road - Ratmalana Sri Lanka Name of authorized Representative : The Chairman, National Water Supply and Drainage Board Galle Road - Ratmalana Sri Lanka The Works consists of ………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………located at ……………….. Intended Completion Date is ………………………. Days from the Start Date. Name of the Contract : …………………………………………….. Contract No. ………………………………………… The office for collection of bid forms is Assistant General Manager (Tenders & Contracts) NWSDB, Galle Road, Ratmalana. The non-refundable fee is Rupees ………………………… Plus VAT, payable in cash The Bid forms will be issued until……………………………. |

| 2.1 | The source of funding is: ………………………………………… |
| --- | --- |
| 4.2 (i) 4.2 (iv) | Minimum qualification to qualify for the award of the Contract is : Experience in Supply and Installation works of at least one contract of a similar nature and complexity equivalent to the supply and Installation works of …….. kW (indicate figure) over the last 5 years. Working Capital *1 + present available credit facilities for the company*2 + credit facilities exclusively for this contract - 0.1 x current work commitments*3>Rs……………*4 *1 Working Capital = Current Assets – Current Liabilities *2 A letter to prove the availability of credit facilities issued by a Bank within a month prior to date of closing of Bids. *3 current work commitment = work remaining uncompleted (Documentary evidence to justify shall be submitted) *4 15% of the estimated cost of the Bid. |
|  | B. Contents of Bidding Documents |
| 7.1 | For Clarification of bid purposes only, the Employer’s address is: Assistant General Manager (Tenders and Contracts), National Water Supply and Drainage Board, Galle Road, Ratmalana. Fax . 011 – 2635885 Tel:011-2605328 |
|  | C. Preparation of Bids |
| 11.1 (o) | The Bidder shall submit the following additional documents: The information listed below shall be submitted with the offer to the Engineer for review. The submittals shall include: - Dimensioned cross sectional drawing of the pump complete with materials of manufacture. - Pump performance curves showing - Head (m) Vs flow (m3/h or l/s) - Pump efficiency Vs flow (m3/h or l/s) - Power required to drive pump (kW) Vs flow (m3/h or l/s) - NPSH Required (m) Vs flow (m3/h or l/s) - All motor information. - Proposed panel layout (indicators, meters, switches etc.) - Specification for MCCB’s, MCB’s, Busbars, Drives etc. - Specification for transducers, sensors etc. - Printed literature – supporting details given in the questionnaire. Revised on 22-03-2023 |
| 17.3 | Period of time the Goods are expected to be functioning. (for the purpose of spare parts: ……………………………………………… |
| 19.1 | The Bid shall be valid for …………………….. Days from the date closing of the bids as specified in the IFB.. |
| 20.1 20.2 20.3 | Bid shall include a Bid Security in the format included in Section 11 Specimen Forms The amount of the Bid Security shall be: Rs. ………………. The validity period of the bid security shall be until………….(give a Date) [This shall be filled by T&C Section] |
|  | D. Submission and Opening of Bids |
| 22.2 (ii) 22.2 (iii) | The inner and outer envelopes shall be addressed to the following address. The Chairman, Cabinet Appointed Procurement Committee, Procurement Division, Ministry of ………………………………………………….., No. 35, “Lakdiya Medura” New Parliament Road, Pelawatta Battaramulla Sri Lanka. Name of the Contract : ……………………………………………. Contract no……………………………………………….. |
| 23.1 | The Procurement Committee’s Address for the submission (an on behalf of the Board) and Bid opening is; The Chairman, Cabinet Appointed Procurement Committee, Procurement Division, Ministry of ………………………………………………….., No. 35, “Lakdiya Medura” New Parliament Road, Pelawatta Battaramulla Sri Lanka. The deadline for the submission of bids is as specified in the IFB Date …………………………… Time ………………………. |

Revised on 10-11-2020

| 26.1 | The place for opening of bids, Procurement Division, Ministry of ………………………………………………….., No. 35, “Lakdiya Medura” New Parliament Road, Pelawatta Battaramulla Sri Lanka. Date …………………………… Time : Immediately after closing of bids |
| --- | --- |
| 35.2 (xii) | - Economic life of Pumping Unit ………. Years.(indicate figure) - Discounting Rate …………….%. (indicate figure) - Power Cost Rs ……/ kWh. (indicate figure) - Annual Operation as mentioned in the particular specification |
| 37.3 | Add the Clause 37.3 If the procurement is within the authority limit of a CAPC. After evaluation of Bids in accordance with the procedures described under Clauses 25, 26, 27, 28, 29, and 30, the Employer will inform to all the bidders in writing the selection of the successful bidder and the intention of contract award to such bidder. The unsuccessful bidders if they so wish, within one week of such notice may make representation to the Secretary to the Ministry of ………………………………………………….. at the address given below. Such representation shall be self-contained to enable the Secretary to arrive at a conclusion and a cash deposit to amount given below shall be made. The Employer may request the bidder who had made representation to submit further evidence during the investigation of such representation. The cash deposit will be forfeited unless the Employer change the original contract award decision in favour of the bidder who has made such representation. Address : The Secretary Appeal Board, Ministry of ………………………………………………….., No. 35, “Lakdiya Medura” New Parliament Road, Pelawatta Battaramulla Cash Deposit : Rs. 100,000.00 |
|  | E. Evaluation and Comparison of Bids |
| 42.1 | Prevailing rate of stamp duty is nil. |
| 43.1 | The amount of performance security shall be ………% of the contract Price |

Revised on 17-06-2024

| 48 | The equipment to be provided under this contract shall be suitable for installation and operation at elevations of about …………………………. M (to be indicated) above sea level inside weather protected structures. Outside ambient temperatures range between ……C and …………… 0C and water temperature varies between ………C and ………C. Relative Humidity is expected to range between …….. and 100%. Atmosphere is dusty. |
| --- | --- |

| Bidding Data (Please note that the clause numbers given here under are that of Instructions to Bidder) The following specific data for the goods and related services to be procured shall complement, supplement, or amend the provisions in the Instructions to Bidders (ITB). Whenever there is a conflict, the provisions herein shall prevail over those in ITB. |  |  |  |
| --- | --- | --- | --- |
| ITB Clause Reference |  | A. General |  |
| 1.1 |  | The Purchaser / Employer is Name: National Water Supply and Drainage Board Address: Galle Road - Ratmalana Sri Lanka Name of authorized Representative : The Chairman, National Water Supply and Drainage Board Galle Road - Ratmalana Sri Lanka The Works consists of ………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………located at ……………….. Intended Completion Date is ………………………. Days from the Start Date. Name of the Contract : ………………………………………………… Contract No.: ………………………………………………. The office for collection of bid forms is Assistant General Manager (Tenders & Contracts) NWSDB, Galle Road, Ratmalana. The non-refundable fee is Rupees ………………………… Plus VAT, payable in cash The Bid forms will be issued until……………………………. |  |
| 2.1 |  | The source of funding is: ………………………………………… |  |
| 4.2 (i) 4.2 (iv) |  | Minimum qualification to qualify for the award of the Contract is : Experience in Supply and Installation works of at least one contract of a similar nature and complexity equivalent to the supply and Installation works of …….. kW (indicate figure) over the last 5 years. Working Capital *1 + present available credit facilities for the company*2 + credit facilities exclusively for this contract - 0.1 x current work commitments*3>Rs……………*4 *1 Working Capital = Current Assets – Current Liabilities *2 A letter to prove the availability of credit facilities issued by a Bank within a month prior to date of closing of Bids. *3 current work commitment = work remaining uncompleted (Documentary evidence to justify shall be submitted) *4 15% of the estimated cost of the Bid. |  |
|  |  | B. Contents of Bidding Documents |  |
| 7.1 |  | For Clarification of bid purposes only, the Employer’s address is: Assistant General Manager (Tenders and Contracts), National Water Supply and Drainage Board, Galle Road, Ratmalana. Fax . 011 – 2635885 Tel:011-2605328 |  |
|  |  | C. Preparation of Bids |  |
| 11.1 (o) |  | The Bidder shall submit the following additional documents: The information listed below shall be submitted with the offer to the Engineer for review. The submittals shall include: - Dimensioned cross sectional drawing of the pump complete with materials of manufacture. - Pump performance curves showing - Head (m) Vs flow (m3/h or l/s) - Pump efficiency Vs flow (m3/h or l/s) - Power required to drive pump (kW) Vs flow (m3/h or l/s) - NPSH Required (m) Vs flow (m3/h or l/s) - All motor information. - Proposed panel layout (indicators, meters, switches etc.) - Specification for MCCB’s, MCB’s, Busbars, Drives etc. - Specification for transducers, sensors etc. Printed literature – supporting details given in the questionnaire. Revised on 22-03-2023 |  |
| 17.3 | Period of time the Goods are expected to be functioning. (for the purpose of spare parts: ……………………………………………… |  |  |
| 19.1 | The Bid shall be valid for …………………….. Days from the date closing of the bids as specified in the IFB. |  |  |
| 20.1 20.2 20.3 | Bid shall include a Bid Security in the format included in Section 11 Specimen Forms The amount of the Bid Security shall be: Rs. ………………. The validity period of the bid security shall be until………….(give a Date) [This shall be filled by T&C Section] |  |  |
|  | D. Submission and Opening of Bids |  |  |
| 22.2 (ii) 22.2 (iii) | The inner and outer envelopes shall be addressed to the following address. The Chairman, Ministry Procurement Committee, Procurement Division, Ministry of ………………………………………………….., No. 35, “Lakdiya Medura” New Parliament Road, Pelawatta Battaramulla Sri Lanka. Name of the Contract : ………………………………………………….. Contract no. …………………………………………………… |  |  |
| 23.1 | The Procurement Committee’s Address for the submission (an on behalf of the Board) and Bid opening is; The Chairman, Procurement Committee, Procurement Division, Ministry of ………………………………………………….., No. 35, “Lakdiya Medura” New Parliament Road, Pelawatta Battaramulla Sri Lanka. The deadline for the submission of bids is as specified in the IFB Date …………………………… Time ………………………. |  |  |

Revised on 22-03-2023

| 26.1 | The place for opening of bids, Procurement Division, Ministry of ………………………………………………….., No. 35, “Lakdiya Medura” New Parliament Road, Pelawatta Battaramulla Sri Lanka. Date …………………………… Time : Immediately after closing of bids |
| --- | --- |
| 35.2 (xii) | - Economic life of Pumping Unit …….. Years.(indicate figure) - Discounting Rate ……………..%. (indicate figure) - Power Cost Rs ………………../ kWh. (indicate figure) - Annual Operation as mentioned in the particular specification |
| 37.3 | Add the Clause 37.3 If the procurement is within the authority limit of a MPC. After evaluation of Bids in accordance with the procedures described under Clauses 25, 26, 27, 28, 29, and 30, the Employer will inform to all the bidders in writing the selection of the successful bidder and the intention of contract award to such bidder. The unsuccessful bidders if they so wish, within one week of such notice may make representation to the Secretary to the Ministry of …………… …………………………………...at the address given below. Such representation shall be self-contained to enable the Secretary to arrive at a conclusion and a cash deposit to amount given below shall be made. The Employer may request the bidder who had made representation to submit further evidence during the investigation of such representation. The cash deposit will be forfeited unless the Employer change the original contract award decision in favour of the bidder who has made such representation. Address : The Secretary Appeal Board, Ministry of ………………………………………….., No. 35, “Lakdiya Medura” New Parliament Road, Pelawatta Battaramulla Cash Deposit : Rs. 25,000.00 |
|  | E. Evaluation and Comparison of Bids |
| 42.1 | Prevailing rate of stamp duty is nil. |
| 43.1 | The amount of performance security shall be ………% of the contract Price |

Revised on 17-06-2024

| 48 | The equipment to be provided under this contract shall be suitable for installation and operation at elevations of about …………………………. m (to be indicated) above sea level inside weather protected structures. Outside ambient temperatures range between …………. and ………… 0C and water temperature varies between …………. and ……………0C. Relative Humidity is expected to range between … . ……….. and 100%. Atmosphere is dusty. |
| --- | --- |

| Bidding Data (Please note that the clause numbers given here under are that of Instructions to Bidder) The following specific data for the goods and related services to be procured shall complement, supplement, or amend the provisions in the Instructions to Bidders (ITB). Whenever there is a conflict, the provisions herein shall prevail over those in ITB. |  |
| --- | --- |
| ITB Clause Reference | A. General |
| 1.1 | The Purchaser / Employer is Name: National Water Supply and Drainage Board Address: Galle Road - Ratmalana Sri Lanka Name of authorized Representative : The Chairman, National Water Supply and Drainage Board Galle Road - Ratmalana Sri Lanka The Works consists of ………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………………located at ……………….. Intended Completion Date is ………………………. Days from the Start Date. Name of the Contract : ……………………………………………. Contract no. …………………………………………………… The office for collection of bid forms is Assistant General Manager (Tenders & Contracts) NWSDB, Galle Road, Ratmalana. The non-refundable fee is Rupees ………………………… Plus VAT, payable in cash The Bid forms will be issued until……………………………. |

| 2.1 | The source of funding is: ………………………………………… |
| --- | --- |
| 4.2 (i) 4.2 (iv) | Minimum qualification to qualify for the award of the Contract is : Experience in Supply and Installation works of at least one contract of a similar nature and complexity equivalent to the supply and Installation works of …….. kW (indicate figure) over the last 5 years. Working Capital *1 + present available credit facilities for the company*2 + credit facilities exclusively for this contract - 0.1 x current work commitments*3>Rs……………*4 *1 Working Capital = Current Assets – Current Liabilities *2 A letter to prove the availability of credit facilities issued by a Bank within a month prior to date of closing of Bids. *3 current work commitment = work remaining uncompleted (Documentary evidence to justify shall be submitted) *4 15% of the estimated cost of the Bid. |
|  | B. Contents of Bidding Documents |
| 7.1 | For Clarification of bid purposes only, the Employer’s address is: Assistant General Manager (Tenders and Contracts), National Water Supply and Drainage Board, Galle Road, Ratmalana. Fax . 011 – 2635885 Tel:011-2605328 |
|  | C. Preparation of Bids |
| 11.1 (o) | The Bidder shall submit the following additional documents: The information listed below shall be submitted with the offer to the Engineer for review. The submittals shall include: - Dimensioned cross sectional drawing of the pump complete with materials of manufacture. - Pump performance curves showing - Head (m) Vs flow (m3/h or l/s) - Pump efficiency Vs flow (m3/h or l/s) - Power required to drive pump (kW) Vs flow (m3/h or l/s) - NPSH Required (m) Vs flow (m3/h or l/s) - All motor information. - Proposed panel layout (indicators, meters, switches etc.) - Specification for MCCB’s, MCB’s, Busbars, Drives etc. - Specification for transducers, sensors etc. - Printed literature – supporting details given in the questionnaire. |

Revised on 22-03-2023

| 17.3 | Period of time the Goods are expected to be functioning. ( for the purpose of spare parts: ……………………………………………… |
| --- | --- |
| 19.1 | The Bid shall be valid for …………………….. Days from the date closing of the bids as specified in the IFB.. |
| 20.1 20.2 20.3 | Bid shall include a Bid Security in the format included in Section 11 Specimen Forms The amount of the Bid Security shall be: Rs. ………………. The validity period of the bid security shall be until………….(give a Date) [This shall be filled by T&C Section] |
|  | D. Submission and Opening of Bids |
| 22.2 (ii) 22.2 (iii) | The inner and outer envelopes shall be addressed to the following address. Assistant General Manager (Tenders & Contracts) National Water Supply & Drainage Board, Galle road, Ratmalana Name of the Contract : ………………………………………………………. Contract no. ………………………………………………………. |
| 23.1 | The Procurement Committee’s Address for the submission (an on behalf of the Board) and Bid opening is; Assistant General Manager (Tenders & Contracts) National Water Supply & Drainage Board, Galle road, Ratmalana The deadline for the submission of bids is as specified in the IFB Date …………………………… Time ………………………. |

Revised on 22-03-2023

| 26.1 | The place for opening of bids, Tenders & Contracts Section, National Water Supply & Drainage Board, Galle road, Ratmalana Date …………………………… Time :Immediately after closing of bids |
| --- | --- |
| 35.2 (xii) | - Economic life of Pumping Unit ………Years.( .(indicate figure) - Discounting Rate ___%. (indicate figure) - Power Cost Rs. ……/ kWh.(indicate figure) - Annual Operation as mentioned in the particular specification |
|  | E. Evaluation and Comparison of Bids |
| 42.1 | Prevailing rate of stamp duty is nil. |
| 43.1 | The amount of performance security shall be ………% of the contract Price |
| 48 | The equipment to be provided under this contract shall be suitable for installation and operation at elevations of about …………………………. m ( to be indicated) above sea level inside weather protected structures. Outside ambient temperatures range between ……….. and …………..0C and water temperature varies between ………. and ………………0C. Relative Humidity is expected to range between …………….. and 100%. Atmosphere is dusty. |

Revised on 29-02-2012

Revised on 17-06-2024

- CONTRACT DATA

The Contract Data is a part of General Conditions of Contract and should be read in conjunction with the General Conditions of Contract.

If there is a discrepancy found in the General Conditions of Contract and the Contract Data, the Content in the Contract Data shall supersede the Content in the General Conditions of Contract.

(Note: What is typed in italic letters are guide lines to prepare the Contract Data and they shall be removed after preparation of the Contract Data.)

| Contract Data (Please note that the Clause nos. given hereunder are that of Conditions of Contract) |  |
| --- | --- |
| The following Contract Data shall supplement and / or amend the Conditions of Contract (CC). Whenever there is a conflict, the provisions herein shall prevail over those in the CC. [The Purchaser shall select insert the appropriate wording using the samples below or other acceptable wording, and delete the text in italics] |  |
| 1.1(g) 1.1(i) 1.1(k) | Defects Liability Period is 365 Days. The Engineer is General Manager, National Water Supply and Drainage Board, Galle Road, Ratmalana. The Purchaser / Employer is Name: National Water Supply and Drainage Board, Address: Galle Road, Ratmalana Name of Authorized Representative: The Chairman, National Water Supply & Drainage Board,: |
| 1.1 (o) 1.1 (u) 1.2 | The Project Site(s)/Final Destination(s) is/are: The Start Date shall be 14 Days from the Letter of Acceptance. Name of Engineer's Representative: ______________ (Fill the Name of Project Director / Deputy General Manager of relevant RSC and Designation) Revised on 22-05-2019 |
| 8.1 | For notices, the Purchaser’s address shall be: Attention: Address: Telephone: Facsimile number: Electronic mail address: |
| 11.1 11.4 | The Works consists of ……………………………………………………………………………………………………………………….……………………………………………………………………………………………………………………………………………… Contract period is …………………………….. |
| 12.1 | Details of Shipping and other Documents to be furnished by the Supplier are, |

Work programme including Procurement of Pumps & Motor and Accessories

Installation drawings

Testing procedures

Technical literatures

Operation & Maintenance Manual

Drawings

Technical details required for Training of Operation Staff

All documents requested for payment in Clause 15 hereof

All Technical details for Automation (if applicable only)

Surge calculation (if applicable)

Technical literatures of Surge Protection System (Electrical/Hydraulic)

Any other document requested by the Employer/ Engineer

Revised on 22-03-2023

| 13.27.1 13.27.2 15.4 |  | Contractor shall supply operation and maintenance manuals before the testing of pumps at site and as built drawing within two weeks from the date of completion of the work. The Engineer shall withhold 5% of the Initial Contract Price. Retention on Payments : 10% of each Payment Limit of Retention : 5% of Contract Price. |
| --- | --- | --- |
| 23 |  | The minimum insurance covers shall be : (a) The minimum cover for insurance of the Works and of Plant and Materials is 110% of the Initial Contract Price. ###### The maximum deductible for insurance of the Works and of Plant and Materials is 5% of the Initial Contract Price. (b) The minimum cover for loss or damage to Equipment is the replacement cost of of equipment The maximum deductible for insurance of Equipment is 5% of the replacement cost of the equipment |
|  |  | (c) The minimum cover for personal injury or death, for third party and employees of the Employer and other persons engaged by the Employer in the Works is Rs 1,000,000 per event, number of events are unlimited |
|  |  | (d) The minimum cover for personal injury or death, - for the Contractor's workmen is Rs 1,000,000 per event, number of events are unlimited. - Contractor's employees other than workmen is Rs 1,000,000 per event, number of events are unlimited. |
| 23.8 25.1 |  | Marine Insurance shall be in an amount equal to 110% of the CIF value of the goods from “warehouse to warehouse” on “all risk” Basis. Tests to be performed as per the Specification Material Performance Assembling Any other test which affect for the durability and the trouble free operation of the good |
|  |  | Inspections to be done Manufacture’s test - Comprehensive Independent Inspection Agency - Comprehensive Pre-shipment inspection by NWSDB Officers shall be …………[State whether comprehensive or not ]. |
| 26.1 |  | Liquidated damages is Rs………….. per Day The maximum amount of liquidated damages shall be:10% of the Contract Price Revised on 22-05-2019 |
| 27.3 27.5 | The comprehensive warranty shall be valid up to three years from the date of taking over for trouble free operation. The warranty shall cover following items/parts. (Generally Pumps and Motors) …………………………………………………………………………………… Attend to repairs within …………….. Days from the Notification. |  |
| 43 | The contractor shall provide the following in three copies at least 14 Days before handing over of the equipment. - Certified copies of all performance test results of pumps and motors. - Manufacturer’s Certification that all pumping units, motor control equipment is fully in conformance with the specification along with shipping documents. - Operation and Maintenance manuals of Pumps and Motors. - Control wiring diagrams for Electrical Panels. (Including Automatic Controls). - Spare Parts Manuals. |  |

Revised on 22-05-2019

Revised on 22-05-2019

Delivery Schedule

| Item No. | Description of Goods | Quantity | Unit | Final Destination [insert place of Delivery] | Delivery Date |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | Purchaser’s delivery date as per the contract |
| 01 | Pumps |  |  |  |  |
| 02 | Motor |  |  |  |  |
| 03 | Accessories |  |  |  |  |

Revised on 24-12-2021

PAYMENT SCHEDULE

Letter of Credit will be opened by the Purchaser. No Advance payment will be made.

| STAGE OF PAYMENT |  | STAGE OF CONTRACT |  | DOCUMENT TO BE SUBMITTED |  | AMOUNT OF PAYMENT |  | REMARKS |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| (A) Foreign Payment |  |  |  |  |  |  |  |  |  |
| 1 | First installment | On shipping the items part or fully |  | - Copies of the Supplier’s invoice showing description of Goods, quantity, unit price, total amount and HS Code Number; - 3 copies of clean on-board bill of lading marked freight prepaid. - Copies of packing list identifying contents of each package and measurements - Manufacturer’s warranty certificate as per Clause 15 hereof. - Inspection certificates, issued by the nominated inspection agency. - Manufacturer’s Inspection and Test Certificate - Certificate of origin - Certificate of conformity to the requirements specified in the specifications. - Inspection and test certificate by the NWSDB pre-shipment Inspection team. |  | 75% of foreign component of the items shipped on Letter of Credit. |  |  |  |
| 2 | Balance foreign component | Final acceptance by the Engineer based on the delivery and other obligations. |  | On production of a Final Acceptance Certificate issued by the Engineer. Engineer’s Representative’s approval for the balance payment of Foreign Component. Submission of Bank guarantee for 5% of Contract Price as a retention money. |  | Balance 25% of the foreign component . |  | The Foreign component of Contract Sum shall become payable within 60 Days from the date of the Engineer’s Final Acceptance Certificate. |  |
| (B) Local Payment |  |  |  |  |  |  |  |  |  |
| 3 | First Payment of supply bill |  | On delivery and stacking of the Goods at site |  | Document providing the delivered Goods and passed in test performed are in compliance with the specifications. |  | 90% of the Local component of the Contract Price less Bank charges |  | Sri Lanka Rupees component by a cheque in favour of the supplier. |
| 4 | Balance Local Payment of supply bill |  | Final acceptance by the Engineer for the delivery and other obligations |  | A written request for balance payment in the form of an invoice based on the BOQ and Engineer’s approval for the payment. |  | 10% of the Local component of the Contract Price less remaining Bank charges. |  | The total Contract Sum shall become payable within 60 Days from the date of the Engineer’s Final Acceptance Certificate. |
| 5 | Installation Bill (Local ) payment |  | On Final Acceptance Certificate. |  | A written request for the Engineer’s Representative’s approval for the payment. |  | As requested by the Contractor in their offer. |  |  |

Revised on 17-06-2024

6.  SPECIFICATIONS

| ### SPECIFICATION FOR SUPPLY & INSTALLATION OF AUTO COUPLING TYPE WET WELL ELECTRICALY DRIVEN SUBMERSIBLE PUMPS AND ACCESSORIES (WET WELL ABOVE 30 KW) | ### 6af-1 to 6af-19 |
| --- | --- |
| ### SPECIFICATION FOR SUPPLY & INSTALLATION OF AUTO COUPLING TYPE DRY WELL ELECTRICALY DRIVEN SUBMERSIBLE PUMPS AND ACCESSORIES (DRY WELL ABOVE 30 KW) | ### 6ah-1 to 6ah-18 |

7.  SCHEDULE OF PARTICULARS

- WET/DRY WELL above 30kW

### SCHEDULE  OF PARTICULARS FOR

### AUTO COUPLING

### TYPE WET/DRY WELL ELECTRICALY DRIVEN

### SUBMERSIBLE PUMPS AND ACCESSORIES

### (Out put hydraulic power  Above 30 kw at the specified operating point as per the specification)

WET/DRY WELL above 30 kW

### SUPPLY & INSTALLATION OF AUTO COUPLING TYPE WET/ DRY WELL ELECTRICALY DRIVEN SUBMERSIBLE PUMPS

### AND ACCESSORIES

# SCHEDULE OF PARTICULARS

- NOTES

1.	The Bidder shall complete the questionnaire pertaining to the equipment, which he offers, and return with his tender and give all details relevant to the equipment offered.

2.	All equipment shall be interconnected electrically and mechanically and all necessary wiring, earths etc. on the load side of the circuit breaker, fuses, identification labels and sundries shall be supplied. Wiring is to be in PVC conduit where necessary.

3.	All equipment shall be capable of operation in a damp tropical climate, with temperature between 20 0C and 40 0C (60 0F and 104 0F) and relative humidity of 70% to 100%.

4.	Each unit or complete equipment shall be provided with a diagram of connection on a plate of metallic or other materials, fixed in a suitable place.

5.	Unless otherwise specified, all materials, equipment and protective devices shall conform to the relevant B.S.S. and to the requirements of the Ceylon Electricity Board.

6.	All test results, literature, manuals, spares lists etc. shall be supplied with the equipment at the time the equipment is delivered at site and the supply of equipment shall not be considered as complete for purpose of payment until the documents specified are delivered.

7.	Important:

The Bidder should fill in completely the Questionnaire attached herewith. The tender is liable to be rejected if the required details are not furnished.

  - Pumps & Accessories

This questionnaire shall be filled by the Bidder and supported with manufacturer’s printed technical literature for each pumping station.  If any information given in the questionnaire is found to differ at the final handing over, the contractor shall be held responsible for it and cost of improvement to meet the indicated specifications shall be recovered from any payments due to the contractor.

A separate schedule is to be provided for each different model number of pump hiring supplied.

Revised on 04-11-2022

| No. | Description | NWSDB Requirement | Bidder’s Proposal |
| --- | --- | --- | --- |
| 1.1.1 | ISO 9001:2015 Quality Management System Certificate available for manufacturer’s work: |  |  |
| 1.1.2 | Make and country of manufacturer : |  |  |
| 1.1.3 | Country of origin : |  |  |
| 1.1.4 | Type/Model No : |  |  |
| 1.1.5 | Shaft Material & Relevant Standard: |  |  |
| 1.1.6 | Casing Material & Relevant Standard: |  |  |
| 1.1.7 | Material and internal coating of the housing and thickness |  |  |
| 1.1.8 | Number of Stages : |  |  |
| 1.1.9 | Delivery Diameters of Pumps : |  |  |
| 1.1.10 | Impeller trimmed or original |  |  |
| 1.1.11 | Actual Impeller diameter |  |  |
| 1.1.12 | Nominal Operation Speed (rpm) |  |  |
| 1.1.13 | Capacity at specified head L/s : |  |  |
| 1.1.14 | Capacity at 10% less head L/s : |  |  |
| 1.1.15 | Capacity at 10% more head L/s : |  |  |
| 1.1.16 | Pump efficiency at specified head % : |  |  |
| 1.1.17 | Shut off head of pump unit : |  |  |
| 1.1.18 | Type of lubricant (oil) in the seal chamber (details of the oil should be mentioned) : |  |  |
| 1.1.19 | Pump Bearing Numbers : |  |  |
| 1.1.20 | Size of the solid particles can be handled : |  |  |
| 1.1.21 | Impeller type & material, relevant material standard : |  |  |
| 1.1.22 | Impeller coating detail and coat thickness : |  |  |
| 1.1.23 | Pump and motor coating details and thickness : |  |  |
| 1.1.24 | Upper and lower seal material: |  |  |
| 1.1.25 | Details of Best Efficiency Point (BEP) |  |  |
|  | - Capacity |  |  |
|  | - Head |  |  |
|  | - Power |  |  |
|  | - Efficiency |  |  |
| 1.1.26 | Details of Operating Point (OP) |  |  |
|  | - Capacity |  |  |
|  | - Head |  |  |
|  | - Power |  |  |
|  | - Efficiency |  |  |
| 1.1.27 | Pump material details : |  |  |
|  | (A) Casing material: |  |  |
|  | - Material testing report provide or not |  |  |
|  | - Relevant material standard |  |  |
|  | - Equivalent BS/DIN/JS/EN-GJS Standard |  |  |
|  | (B) Impeller material |  |  |
|  | - Material testing report provide or not |  |  |
|  | - Relevant material standard |  |  |
|  | - Equivalent BS/DIN/JS/EN-GJS Standard |  |  |
| 1.1.28 | Paint details (If paint is available, following should be clearly specify) a). Impeller: |  |  |
|  | - Type of paint |  |  |
|  | ii. No of Coating |  |  |
|  | iii. Thickness of coating |  |  |
|  | iv. Paint supplier address |  |  |
|  | b). Pump Casting Internal paint details: |  |  |
|  | - Type of paint |  |  |
|  | ii. No of Coating |  |  |
|  | iii. Thickness of coating |  |  |
|  | iv. Paint supplier address | Revised on 04-11-2022 |  |
|  | c). Pump and Motor Exernal paint details: |  |  |
|  | - Type of paint |  |  |
|  | ii. No of Coating |  |  |
|  | iii. Thickness of coating |  |  |
|  | iv. Paint supplier address |  |  |

Motor

Revised on 04-11-2022

| No. | Description | NWSDB Requirement | Bidder’s Proposal |
| --- | --- | --- | --- |
| 1.2.1 | Is ISO 9001: 2015 Quality Management System Certificate available for manufacturer’ |  |  |
| 1.2.2 | Make and Country of Manufacture: |  |  |
| 1.2.3 | Type/Model No. |  |  |
| 1.2.4 | Class of Insulation: |  |  |
| 1.2.5 | Temperature rise after 6 hours operation: |  |  |
| 1.2.6 | Nominal operating voltage : |  |  |
| 1.2.7 | Nominal operating frequency (Hz) : |  |  |
| 1.2.8 | Full load speed (RPM) |  |  |
| 1.2.9 | Number of Phases : |  |  |
| 1.2.10 | Allowable Supply Voltage fluctuation + % : |  |  |
| 1.2.11 | Rated output KW : |  |  |
| 1.2.12 | Power factor (Full load) : |  |  |
| 1.2.13 | Power factor (3/4 load) : |  |  |
| 1.2.14 | Power factor (1/2 load) : |  |  |
| 1.2.15 | Current (Full load) A : |  |  |
| 1.2.16 | Current (No load) : |  |  |
| 1.2.17 | Degree of Protection of enclosure : |  |  |
| 1.2.18 | Starting current : |  |  |
| 1.2.19 | Motor Bearing Numbers : |  |  |
| 1.2.20 | Motor efficiency at duty point : |  |  |
| 1.2.21 | Are thermal sensors installed? |  |  |
| 1.2.22 | Motor cooling method |  |  |
| 1.2.23 | Maximum possible number of starts per hour |  |  |
| 1.2.24 | Are moisture detectors installed? |  |  |
| 1.2.25 | Water in oil sensor available or not |  |  |

General for Pumps & Accessories

Revised on 04-11-2022

| No. | Description | NWSDB Requirement | Bidder’s Proposal |
| --- | --- | --- | --- |
| 1.3.1 | Total weight of the unit |  |  |
| 1.3.2 | Overall efficiency at duty point : |  |  |
| 1.3.3 | Local agent, if available : |  |  |
| 1.3.4 | No of similar pumps installed in Sri Lanka : |  |  |
| 1.3.5 | Maximum allowable water temp : |  |  |
| 1.3.6 | Maximum Overall diameter of Unit : |  |  |
| 1.3.7 | Maximum allowable ambient temperature : |  |  |
| 1.3.8 | Power absorbed by the pump at duty point |  |  |
| 1.3.9 | Minimum operating head of the pump and relevant capacity: |  |  |
| 1.3.10 | Power absorbed at operating point given in the above item No. 10: |  |  |
| 1.3.11 | Pump efficiency at operating point given in the above Item No. 10. |  |  |
| 1.3.12 | What are the special features in the system incorporated for withstanding corrosive atmosphere: |  |  |
| 1.3.13 | Details of the registered workshop and facilities available |  |  |
| 1.3.14 | After sales service, available |  |  |

  - DUCTILE IRON PIPES AND FITTINGS

1.4.a 	Flanged pipes

Revised on 04-11-2022

| No. | Description | NWSDB Requirement | Bidder’s Proposal |
| --- | --- | --- | --- |
| 1.4.a i | Name & Address of Manufacturer's factory: |  |  |
| 1.4.a ii | Name and address of the Manufacturer's Agent in Sri Lanka: |  |  |
| 1.4.a iii | Port of shipment: |  |  |
| 1.4.a iv | Manufacturing Process: |  |  |
| 1.4.a v | - Class of pipe : |  |  |
|  | - Standard to which pipes conform to: |  |  |
|  | - Standard to which flanges conform to |  |  |
| 1.4.a vi | Gaskets for flanged joints: |  |  |
|  | - Standard to which the product conforms to : |  |  |
|  | - Material : |  |  |
| 1.4.a vii | Bolts for flanges: |  |  |
|  | Dia. Length No. off for 1 set Material |  |  |
| 1.4.a viii | Thickness of internal lining: |  |  |
|  | - Cement |  |  |
|  | - Cement type used for lining |  |  |
| 1.4.a ix | Thickness of external coating: |  |  |
|  | - Bitumen |  |  |
|  | - Zinc |  |  |
| 1.4.a x | Protection of pipes and pipe ends in transit: |  |  |
| 1.4.a xi | Nature of casting (i.e. Integrally Cast or welded): |  |  |
| 1.4.a xii | State whether welding is done under factory conditions at the point of manufacture in the case of welded pipes: |  |  |
| 1.4.a xiii | Availability of ISO 9001: 2015 Certificate for Quality Management System: |  |  |
| 1.4.a xiv | Indicate whether manufacturer’s Identification mark cast/embossed on pipes: |  |  |

1.4. b.	Fittings (except Tees)

| No. | Description | NWSDB Requirement | Bidder’s Proposal |
| --- | --- | --- | --- |
| 1.4. b i | Name & Address of Manufacturer's factory: |  |  |
| 1.4. b ii | Name & Address of Manufacturer's Agent in Sri Lanka: |  |  |
| 1.4. b iii | Port of shipment: |  |  |
| 1.4. b iv | Manufacturing Process: |  |  |
|  | - Class of pipe: |  |  |
|  | - Standard to which fittings conforms to |  |  |
|  | - Standard to which flanges conform to |  |  |
| 1.4. b v | Ring for Tyton Joint: |  |  |
|  | - Standard to which product conforms to: |  |  |
|  | - Material: |  |  |
| 1.4. b vi | Bolts for flanges: |  |  |
|  | Dia. Length No. off for 1 set Material |  |  |
| 1.4. b vii | Thickness of internal lining: |  |  |
|  | - Cement |  |  |
|  | - Cement type used for lining |  |  |
| 1.4. b viii | Thickness of external coating: |  |  |
|  | - Bitumen |  |  |
|  | - Zinc |  |  |
| 1.4. b xi | Nature of casting (i.e. Integrally cast or welded): |  |  |
| 1.4. b x | State whether welding is done under factory condition at the point of manufacture in the case of welded fittings. |  |  |
| 1.4. b xi | Protection of fittings in transit : |  |  |
| 1.4. b xii | Availability of ISO 9001: 2015 Certificate for Quality Management System: |  |  |
| 1.4. b xiii | Indicate whether manufacturer’s Identification mark cast/embossed on fittings: |  |  |

Revised on 04-11-2022

1.4.c.	Tees

| No. | Description | NWSDB Requirement | Bidder’s Proposal |
| --- | --- | --- | --- |
| 1.4.c i | Name & Address of Manufacturer's factory: |  |  |
| 1.4.c ii | Name and address of the Manufacturer's Agent in Sri Lanka: |  |  |
| 1.4.c iii | Port of shipment: |  |  |
| 1.4.c iv | Manufacturing Process: |  |  |
|  | - Class of tees: |  |  |
|  | - Standard to which tees conform to: |  |  |
|  | - Standard to which flanges conform to |  |  |
| 1.4.c v | Ring for Tyton Joint: |  |  |
|  | - Standard to which product conforms to: |  |  |
|  | - Material: |  |  |
| 1.4.c vi | Bolts for flanges: |  |  |
|  | Dia. Length No. off for 1 set Material |  |  |
| 1.4.c vii | Thickness of internal lining: |  |  |
|  | - Cement |  |  |
|  | - Cement type used for internal lining |  |  |
| 1.4.c viii | Thickness of external coating: |  |  |
|  | - Bitumen |  |  |
|  | - Zinc |  |  |
| 1.4.c ix | Nature of casting (i.e. Integrally cast or welded): |  |  |
| 1.4.c x | State whether welding is done under factory conditions at the point of manufacture in the case of welded tees. |  |  |
| 1.4.c xi | Protection of fittings in transit: |  |  |
| 1.4.c xii | Availability of ISO 9001: 2015 Certificate for Quality Management System: |  |  |
| 1.4.c xiii | Indicate whether manufacturer’s Identification mark cast/embossed on tees: |  |  |

Revised on 04-11-2022

1.4.d.   Flanged Adaptors and Couplings

| No. | Description | NWSDB Requirement | Bidder’s Proposal |
| --- | --- | --- | --- |
| 1.1.4.d i | Name & Address of Manufacturer's factory: |  |  |
| .1.4.d ii | Name and address of the Manufacturer's Agent in Sri Lanka: |  |  |
| .1.4.d iii | Name and address of the Manufacturer's Agent in Sri Lanka: |  |  |
|  | - Manufacturing Process: |  |  |
|  | - Standards to which flanged adaptors and couplings conforms to : |  |  |
| .1.4.d iv | Ring for Adaptors & couplings: |  |  |
|  | - Standard to which the product conforms: |  |  |
|  | - Material: |  |  |
|  | - Standard to which flanges conform to |  |  |
| .1.4.d v | Bolts for coupling and flange Adaptor: |  |  |
| . | - Dia. Length No. off for 1 set Material |  |  |
| 1.4.d vi | Details of corrosion protection: |  |  |
| .1.4.d vii | Protection of flanged adaptors and Couplings in transit : |  |  |
| .1.4.d viii | Protection for buried Flange Adaptors (Materials proposed and quantities for each size adaptor): |  |  |
| 1.4.d ix | - Availability of ISO 9001: 2015 Certificate for Quality Management System: |  |  |
| 1.4.d x | Indicate whether manufacturer’s Identification mark cast/embossed on couplings: |  |  |

Revised on 04-11-2022

1.4.e.	VALVES & ACCESSORIES

A separate schedule is to be provided for each size of valve being supplied

Revised on 04-11-2022

| No. | Description | NWSDB Requirement | Bidder’s Proposal |
| --- | --- | --- | --- |
| 1.4.e i | Name & Address of the Manufacturer's factory: |  |  |
| 1.4.e ii | Name and address of the Manufacturer's Agent (if any) in Sri Lanka : |  |  |
| 1.4.e iii | Port of shipment: |  |  |
| 1.4.e iv | Time for delivery of materials: |  |  |
|  | - Gate valves: |  |  |
|  | - Reflux valves: |  |  |
| 1.4.e v | Packing and protection of valves in transit: |  |  |
|  | - Gate valves: |  |  |
|  | - Reflux valves: |  |  |
| 1.4.e vi | Description of valves and reference to accompanying catalogue/pamphlets (if any) |  |  |
|  | - Gate valves: |  |  |
|  | - Reflux valves: |  |  |
| 1.4.e vii | Specify the Standards to which the following items to be supplied under this contract comply with: |  |  |
|  | - Gate valves: |  |  |
|  | - Reflux valves: |  |  |
| 1.4.e viii | Material of: |  |  |
|  | - Valve body: |  |  |
|  | - Valve Stem |  |  |
| 1.4.e ix | Pressure rating of flanges: |  |  |
| 1.4.e x | Standard to which flanges conform to |  |  |
| 1.4.e xi | External protection details of valve: |  |  |
| 1.4.e xiii | Indicate whether manufacturer’s Identification mark cast/embossed on valves: |  |  |
| 1.4.e xiv | What is the type of no return valve (Ball type, Swim type, liver type |  |  |
| 1.4.e xv | Type of Non return valve |  |  |
|  | - Non –slam closure available or not (Explain the non slamming mechanism with literature) |  |  |
|  | - Rapid closure type or not(Explain the rapid closing mechanism with literature) |  |  |
|  | - Adjustable weights available or not |  |  |
|  | - Can be adjust the Rapid closure time (Explain the mechanism with literature) |  |  |
|  | - Material of Body |  |  |
|  | - Materials of Ball or disk |  |  |

Revised on 04-11-2022

  - General for DI Pipes, Valves, Fittings & Specials

1.5.1	DI Pipes, Fittings & Specials

1.5.1.1	 Name and address of the Insurance Corporation/Company, which will insure the materials between the place of manufacture and the final point of delivery:

1.5.1.2  Time for delivery of materials

| - Material | Date of Shipping | Date of Delivery At Site |
| --- | --- | --- |
| 1. Flanged pipes |  |  |
| 2. Fittings |  |  |
| 3. Adaptors & Couplings |  |  |
| 4. Accessories |  |  |

    - Indicate whether all DI pipes, tees, bends & reducers are from the same source of manufacture (DI pipes & fittings from different sources of manufactures will not be accepted)

    - Supplies of similar nature carried out during the last three years.

    - Indicate whether ISO 9001:  2015 series for Quality Management System obtained for following products.

| Material | ISO 9001: 2015 Quality Management System obtained (Yes/No) |
| --- | --- |
| 1. Flanged pipes |  |
| 2. Fittings |  |
| 3. Adopters & Couplings |  |
| 4. Accessories |  |

Revised on 04-11-2022

1.5.2	Valves

1.5.2.1	 Name and address of the Insurance Corporation/Company, which will insure the materials between the place of manufacture and the final point of delivery:

      - Time for delivery of materials

| - Material | Date of Shipping | Date of Delivery At Site |
| --- | --- | --- |
| 1. Gate Valves |  |  |
| 2. Reflux Valves |  |  |
| 3. Accessories |  |  |

      - Supplies of similar nature carried out during the last three years.

1.5.2.3 Indicate whether ISO 9001:  2015 series for Quality Management System

obtained for following products.

| - Material | ISO 9001: 2015 Quality Management System obtained (Yes/No) |
| --- | --- |
| 1. Gate Valves |  |
| 2. Reflux Valves |  |
| 3. Accessories |  |

  - CONTROL PANEL

A separate schedule is to be provide for each control panel.

Revised on 04-11-2022

| No. | Description | NWSDB Requirement | Bidder’s Proposal |
| --- | --- | --- | --- |
| 1.6.1 | Capacity of incoming pannel (kW) |  |  |
| 1.6.2 | Capacity of each starter (kW) |  |  |
| 1.6.3 | Name of manufacture of the panel: |  |  |
| 1.6.4 1.6.5 | Make, model, rating and breaking capacity of MCCB in: |  |  |
|  | - Incoming section |  |  |
|  | - Motor starting section |  |  |
|  | - Auxiliary section Interlocking in the off position available |  |  |
| 1.6.6 | Make and capacity of the contractors in the panel |  |  |
| 1.6.7 | Make, Model and range of relays |  |  |
|  | a) Overload relays |  |  |
|  | - Time delay |  |  |
|  | - Voltage monitoring |  |  |
|  | - Phase protection |  |  |
|  | - Earth leakage |  |  |
|  | - Other (Specify every relays in the panel) |  |  |
| 1.6.8 | Make of panel enclosure and whether complies with the specifications. |  |  |
| 1.6.9 | Details of earth fault protection |  |  |
|  | - Type |  |  |
|  | - Make & Model |  |  |
|  | - Ratings |  |  |
|  | - Short circuit capacity (kA) |  |  |
| 1.6.10 | Details of the junction boxes |  |  |
| 1.6.11 | Details of auto transformer (tapping ratios should be mentioned) |  |  |
| 1.6.12 | Thermal overloads available for the auto transformer |  |  |
| 1.6.13 | Control voltage |  |  |
| 1.6.14 | Enclose paint details |  |  |
|  | - Type of paint |  |  |
|  | - No of Coating |  |  |
|  | - Thickness of coating |  |  |
|  | - Paint supplier address |  |  |
| 1.6.15 | Power incoming section |  |  |
|  | - Whole panel dimensions & weight |  |  |
|  | - Power incoming section dimensions & weight |  |  |
|  | - Ammeter range |  |  |
|  | - Voltmeter range |  |  |
|  | - Cos Ø meter range |  |  |
|  | - Details of indicating bulbs | Revised on 04-11-2022 |  |
| 1.6.16 | Power motor starting section |  |  |
|  | - Whole panel dimensions & weight |  |  |
|  | - Power incoming section dimensions & weight |  |  |
|  | - Voltmeter range |  |  |
|  | - Cos Ø meter range |  |  |
|  | - Details of indicating bulbs |  |  |
| 1.6.17 | Cable |  |  |
| 1.6.17.1 | Cable from Change over to panel to incoming section |  |  |
|  | - Make |  |  |
|  | - Type |  |  |
|  | - Size (mm2) |  |  |
| 1.6.17.2 | Cable from incoming section to starter |  |  |
|  | - Make |  |  |
|  | - Type |  |  |
|  | - Size (mm2) |  |  |
| 1.6.17.3 | Submersible motor Cable (Starter to motor) |  |  |
|  | - Make |  |  |
|  | - Type |  |  |
|  | - Size (mm2) |  |  |
| 1.6.17.4 | Control cables |  |  |
|  | - Make |  |  |
|  | - Type |  |  |
|  | - Size (mm2) |  |  |

Revised on 04-11-2022

| Description | Make | Size (mm2) | Type (Core/Armour) | Material (Cu/Al) | Length |
| --- | --- | --- | --- | --- | --- |
| 1 Cable from CEB panel to starter |  |  |  |  |  |
| - Cable from motor starter to junction box |  |  |  |  |  |
| - Submersible motor cable |  |  |  |  |  |
| - Control cables |  |  |  |  |  |

8.   DEVIATION FROM SPECIFICATION

DEVIATIONS FROM SPECIFICATIONS

Preamble

The Bidder is required to list any deviations of materials workmanship etc. from the Specifications including such information as has already been given elsewhere in the Bidding Documents. The information shall be in sufficient detail to enable the Engineer to make a realistic assessment of the effect of such deviations on the performance or life of the materials to be supplied and also such deviation if any shall be subject to Clause 29 of Instructions to Bidders.

The list shall also include deviations from the Specifications relating to the mode of operation and/or control of any item of equipment, and any deviations from the specified design requirements for plant components.

Deviations

Note:

Additional sheets should be attached as necessary

9. List of Drawings

LIST OF DRAWINGS

| Drg. No. | # Description |
| --- | --- |

10 .  BILL OF QUANTITIES

### SUPPLY& INSTALLATION OF ……………………………………….………………………………………… PUMPS AND ACCESSORIES

BILL OF QUANTITIES

## NOTES

1.	Documents to be read in conjunction with the Bill of Quantities

1.1	Attention is directed to the Form of Bid, Notice to Bidders, Instructions to Bidders, Conditions of Contract, Specifications and Appendices, which are to be read in conjunction with the Bill of Quantities.

2.	Description of Items

2.1	General obligations and general descriptions of work and material given in the Conditions of Contract and the Specifications are not necessarily repeated in the Bill of Quantities.

2.2	Descriptions attached to the items in the Bills of Quantities are only sufficient detail to ensure identification of the work described in the Specification.

2.3	Reference is to be made to the Conditions of Contract, Specifications and the Appendices for detailed information.

3.	Contracts to be priced completely

3.1	The Bidders may price one or more of the Bills in the Bill of Quantities. Each priced bill must be complete by itself and the final summary, covering all bills, must be completed.

4.	Rates and Prices to be fully inclusive

4.1	In pricing the items of the Bills, the Bidder shall cover himself and will be deemed to have covered himself for:-

a)	All services and materials which according to the true intent and meaning of the contract may be reasonably inferred as necessary for completion of delivery/installation of the materials and equipment in sound condition to the site as indicated in the schedule of requirements.

b)	All obligations, liabilities and responsibilities that the Contract Documents place upon the Bidders in connection with or in relation to the Contract.

4.2	The Bidder shall include in his Bided prices, unless itemised separately for :-

- All costs arising out of inspection and testing at the place of manufacture.

- All costs of packing as specified or as required for export overseas and storage.

- All costs and insurances of delivering the materials to the site/stores as indicated in the Schedule of Requirements.

- All costs incurred in the installation of pumps/control panels and all necessary accessories according to the drawings and specifications.

5.	Bids with unit prices which are so unbalanced as to be detrimental to the Employer's interests may be rejected or cause rejection, at the discretion of the Employer.

6.	Unit rates accepted by the Employer shall be held good and effective until the work is completed and accepted by the Employer.

7.	A rate and/or price is to be entered against each item in the Bill of Quantities whether quantities are stated or not. The cost of any item against which a rate has not been entered shall be deemed to be covered by other rates in the corresponding bill.

8.	All bends, tees & reducers shall be from a single source of manufacture.  Fittings from different sources of manufactures shall not be accepted. ISO 9001 : 2015 for quality assurance issued by a accredited body should be forwarded along with the Bid for all items offered.

9.	Cost of combined allowance  for pre-shipment inspection for two Engineers by the Employer shall be for the entire duration as per the Clause 8.2 of the Conditions of Contract.  If any shortage is found, the supplier shall bear the additional cost.

10.	Cost of Inspection and Testing by the Independent Inspection and Testing Agency shall be as per the Clause 25 of the Conditions of Contract.

- SUPPLY OF AUTO COUPLING TYPE WET/DRY WELL ELECTRICALY DRIVEN SUBMERSIBLE PUMPS

- AND ACCESSORIES

CONTRACT No. ………………………………….

BILL OF QUANTITIES

BILL No 01: General Bill

| Item No. | Description | Qty. | Unit | Rate | Amount |
| --- | --- | --- | --- | --- | --- |
|  |  |  |  | LKR. | LKR. |
| 1 | Allow for all insurance works to be provided during Installation period for the items in this bill. |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
|  | Total of page No. 10- 3 carried to Summary in page 10 – ….. |  |  |  |  |

Revised on 17-06-2024

- SUPPLY OF AUTO COUPLING TYPE WET/DRY WELL ELECTRICALY DRIVEN SUBMERSIBLE PUMPS

- AND ACCESSORIES

CONTRACT No. ………………………………….

SUMMARY OF BILL NO. 01

| Page Number | Amount |
| --- | --- |
|  | Local (LKR.) |
| Page No. 10 - 3 |  |
| Total of Page No.10 - …. Carried to Summary of Bills in Page No. 10 - ….. |  |

Revised 17-06-2024

### SUPPLY& INSTALLATION OF ……………………………………….………………………………………… PUMPS AND ACCESSORIES

CONTRACT No. ………………………………….

BILL OF QUANTITIES

BILL No 02: Supply Bill

| Item No. | Description | Qty. | Unit | Rate |  | Amount |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Foreign (FOB) USD | Local LKR. | Foreign (FOB) USD | Local LKR. |
| 1 | Supply of wet/dry well auto coupling type electrically submersible sewage pumping sets as specified in the specification of capacity …….. against a total head of ….. with duck foot bend, SS guide rails as shown in the drawing & ….. long Stainless Steel lifting chain as per the specifications. The each pump shall provide minimum of ….. long submersible power cables up to the panel board. (All stainless steel material to be SS316) | 03 | Nos. |  |  |  |  |
| 2 | Supply of Identical Pump above with …..m long Stainless Steel lifting chain and minimum of ……m long submersible power cable as per the specifications. (The pump to be kept at the stores as a spare) | 01 | No |  |  |  |  |
| 3 | Supply of DI pipes & fittings and specials as per the drawing …………………… including, Non return Valves(PN…,DN….), Sluice valves(PN…,DN….), Flange Adaptors, Couplings, with required all necessary accessories(pressure gauges, etc,)to full fill the requirement as per the drawing. (Rate to include all necessary pipes supporting arrangement as per drawing.) | - | Item |  |  |  |  |
| 4 | Supply of floor/wall mounted type electrical panel complete with all necessary accessories, switchgears, cables, earth system, Junction box(IP68) etc, and level monitoring equipments as float sensors/ultrasonic level sensors and their cables for the above pumps as per the specification. | - | Item |  |  |  |  |
|  | Total of page No. 10- ….. carried to Summary in page 10 – ….. |  |  |  |  |  |  |

Revised on 17-06-2024

### SUPPLY& INSTALLATION OF ……………………………………….………………………………………… PUMPS AND ACCESSORIES

CONTRACT No. ………………………………….

BILL OF QUANTITIES

| Item No. | Description | Qty | Unit | Rate |  | Amount |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Foreign (FOB) USD | Local LKR. | Foreign (FOB) USD | Local LKR. |
| 5 | Supply of spares, as specified in specifications for satisfactory operation of the pumps. (Bidder shall submit an itemized and priced list of spares). | - | Item |  |  |  |  |
| 6 | Supply of four complete sets of pump catalogues, manuals, spare parts manuals etc. as specified in specification | - | Item |  |  |  |  |
|  | Total of page No. 10- …. carried to Summary in page 10 – …. |  |  |  |  |  |  |

Revised on 17-06-2024

+

### SUPPLY& INSTALLATION OF ……………………………………….………………………………………… PUMPS AND ACCESSORIES

CONTRACT No. ………………………………….

SUMMARY OF BILL NO. 02

| Page Number | Unit | Amount |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | Foreign (USD) |  | Local (LKR.) |  |
| Page No 10-...... | - |  |  |  |  |
| Page No 10-..... | - |  |  |  |  |
| Freight | Sum |  |  |  |  |
| Cost of Inspection and Testing by Independent Testing & Inspection Ageney as per Clause No. 25.9 | Sum |  |  |  |  |
| Incidental allowance and Combined allowances for Pre – Shipment Inspection for two Engineers by Employer as per clause no 25.9 of Conditions of Contract. No. of Pre-shipment inspection ………….. (to be filled by the bidder) | Sum |  |  |  |  |
| Total of Page No…….. Carried to Summary of Bills in Page No. ….. | - |  |  |  |  |

Revised on 17-06-2024

- SUPPLY OF AUTO COUPLING TYPE WET/DRY WELL ELECTRICALY DRIVEN SUBMERSIBLE PUMPS

- AND ACCESSORIES

CONTRACT No. ………………………………….

BILL OF QUANTITIES

BILL No 03: Installation Bill

| Item No. | Description | Qty. | Unit | Rate | Amount |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | Local (LKR.) |  | Local (LKR.) |
| 1 | Installations of pumps, pipe & fittings and accessories supplied under above Item No 2 & 4. including all necessary supporting arrangements as per drawings (Rate to include for construction of suitable concrete foundations, metal and welding, breaking and making good of walls and floor] | - | Item |  |  |  |
| 2 | Installation of the panel and level monitoring equipment’s supplied under above Item 06 and with all accessories, laying & fixing cables etc. Including construction of panel supporting structures using Grade 20 concrete. | - | Item |  |  |  |
| 3 | Testing and commissioning of all above equipment to the satisfaction of Engineer. | - | Item |  |  |  |
|  | Total of page No. 10-…… carried to Summary in page 10-…… |  |  |  |  |  |

Revised on 17-06-2024

- SUPPLY OF AUTO COUPLING TYPE WET/DRY WELL ELECTRICALY DRIVEN SUBMERSIBLE PUMPS

- AND ACCESSORIES

CONTRACT No. ………………………………….

SUMMARY OF BILL NO. 03

| Page Number | Amount |
| --- | --- |
|  | Local (LKR.) |
| Page No. 10 - ..... |  |
| Total of Page No.10 - ….. Carried to Summary of Bills in Page No. 10 - …. |  |

Revised on 17-06-2024

SUPPLY& INSTALLATION OF AUTO COUPLING TYPE WET/ DRY WELL ELECTRICALY DRIVEN SUBMERSIBLE PUMPS

AND ACCESSORIES

CONTRACT No. ………………………………….

SUMMARY   OF   BILLS

| Bill No. | Description | Amount |  |
| --- | --- | --- | --- |
|  |  | Foreign (FOB) USD | Local (LKR.) |
| 01 | General Bill | …………….. | …………….. |
| 02 | Supply of auto coupling type wet/dry well electrically driven submersible pumps and accessories | …………….. | …………….. |
| 03 | Installation of auto coupling type wet/dry well electrically driven submersible pumps and accessories | …………….. | …………….. |
| 04 | ……………………………………………. | ……………… | …………….. |
| 05 | ……………………………………………. | ……………… | …………….. |
| A | Sub Total 1 carried forwarded to Grand Summary |  |  |

Revised on 17-06-2024

SUPPLY& INSTALLATION OF AUTO COUPLING TYPE WET/ DRY WELL ELECTRICALY DRIVEN SUBMERSIBLE PUMPS

AND ACCESSORIES

CONTRACT No. ………………………………….

GRAND   SUMMARY

| Bill No. | Description | Amount |  |
| --- | --- | --- | --- |
|  |  | Foreign (FOB) USD | Local (LKR.) |
| A | Sub Total 1 |  |  |
| B | Less: Provisional Sums (if any) |  |  |
| C | Sub Total 2 (A-B) |  |  |
| D | Less: Discount (if any) ………….. |  |  |
| E | Sub Total 3 (C-D) |  |  |
| F | Add : Provisional Sums (if any) |  |  |
| G | Sub Total 4 (E+F) |  |  |
| H | Add: Contingencies 10% [for Sub Total 4] |  |  |
| I | Grand Total (G + H) carried to Form of Bid (excluding VAT) |  |  |
| J | VAT (………%) |  |  |
| K | Grand Total Including VAT (I + J) |  |  |

VAT Registration Number:………………………………………………………………..

(A copy of the VAT Registration Certificate shall be annexed.)

Note: - The NWSDB VAT Registration No: - 4090 31820 7000

Revised on 17-06-2024

11.  SPECIMEN   FORMS

- BID SECURITY

- CONTRACT AGREEMENT

- PERFORMANCE GUARANTEE

#### LETTER OF ACCEPTANCE

#### RETENTION MONEY GURANTEE

FORM OF BID SECURITY (Unconditional)

…………………… [issuing agency’s name, and address of  issuing branch or office]

………………………

………………………..

Beneficiary : Chairman

National Water Supply and Drainage Board

Galle Road, Ratmalana

Date………………			BID GUARANTEE No : ………………………

We have been informed that …………………………………………………………. [name of  the Bidder ; if joint venture, list complete legal names of partners] (hereinafter called “the Bidder”) has submitted to you its bid dated ……………….. [insert date] (hereinafter called  “ the Bid”) for the execution / supply of  ……………………………………………………..

.[name of contract]  under Contract No……………………………… .

Furthermore, we understand that, according to your conditions, Bids must be supported by a Bid Guarantee.

At the request of the Bidder, we ……………………………………………………….. [name of issuing agency] hereby irrevocably under take to pay you any sum or sums not exceeding in total an amount of ………………………. [amount in figures] …………………..  ……………………………………….[amount in words] upon receipt by us of  your first demand in writing accompanied by a written statement stating that the Bidder is in breach of its obligation (s) under the bid conditions, because of the Bidder:

(a).	has withdrawn its Bid during the period of  bid validity specified ; or

(b).	does not accept the correction of errors in accordance with the Instructions to Bidders (hereinafter “the ITB” ) or

(c ).	having been notified of the acceptance of its Bid by the Employer/ Purchaser during the period of Bid validity, (i) fails or refuses to execute the Contract Form, if required, or  (ii) fails or  refuses to furnish the Performance Security, in accordance with the ITB.

This Guarantee shall expire: (a) if the Bidder is the successful bidder, upon our receipt of copies of the Contract signed by the Bidder and of the Performance Security issued to you by the Bidder, or (b) if the Bidder is not the successful bidder, upon the earlier of (i) our receipt of a copy of your notification to the Bidder that the Bidder was unsuccessful, otherwise it will remain in force up to ………………… [insert date].

Consequently, any demand of payment under this Guarantee must be received by us the office on or before that date………………………………….

………………………………………………

[Signature (s) of authorized representative (s)]

Revised on 22-03-2023

THE GOVERNMENT OF THE DEMOCRATIC SOCIALIST REPUBLIC OF

SRI LANKA

MINISTRY OF ……………………………………………………………………………

NATIONAL WATER SUPPLY AND DRAINAGE BOARD

SUPPLY AND INSTALLATION OF ………..…………………………………………………..

…………………………………..  PUMPS AND ACCESSORIES

…………………………………….. SEWERAGE SCHEME

CONTRACT No.: ……………………………………

CONTRACT AGREEMENT

Contract Agreement made and entered into between the National Water Supply and Drainage Board, a corporate body duly established under the provisions of the National Water Supply and Drainage Board Law No. 2 of 1974 and having its Head Office at Ratmalana in Sri Lanka (hereinafter sometimes referred to as "the Board") of the one part and Messrs : ………………………………….…….…………….………….................................................. ........................................................which duly incorporated under the laws of Democratic Socialist Republic of Sri Lanka and having registered It's office at ……….................................................................................……………………………………

……………………………………………….(hereinafter called "the Contractor" which term of expression shall where the context so requires or admits mean and include its successors and permitted assigns) of the other part.

WHEREAS the Board is desirous of entering into a contract with the Contractor for the supply and installation of ……………………........…………………..................................... ………………………. to ....................................... at locations as specified in the Delivery Schedule and has accepted a Bid by the Contractor for the execution and completion of such works.

AND WHEREAS the Bills of Quantities or Schedule of Rates and Specifications and General Conditions of Contract describing the Works to be done have been prepared by the Board and the same have been signed by the parties hereto.

NOW it is hereby agreed as follows:

1.	For the consideration hereinafter mentioned the Contractor shall, upon and subject to the conditions hereto annexed, complete the Works referred to in the said Bills of Quantities or Schedule of Rates and in the said Specifications and Conditions of Contract to the entire satisfaction of the Board on or before the.............................................……… ………..............................................…….........................................................…..………………………………………………………………..subject to extras, omissions and variations to be determined by the Engineer as hereinafter provided.

Revised on 10-11-2020

2.	The said General Conditions of Contract, the said Specifications, the said Bills of Quantities or Schedule of Rates, (a detailed list whereof is annexed hereto,) Instructions to Bidders, Contract Data, Bidding Data and Schedule of Particulars and Form of Bid, all duly signed by the Board and the Contractor shall for all purposes whatsoever be read, regarded and construed as part and parcel of the Agreement.

3.	The Contractor will be paid for the said execution of the Works the sum of ……...........................................…...................……(Rs................................) hereinafter sometimes referred to as the "Contract Price" or such as shall become payable hereunder according to the terms of the Contract.

4.	As security for the due and proper performance and fulfillment of this contract and for the due payment of all claims to which the Board may be entitled hereunder, the Contractor hereby undertakes to maintain to the Board with a Guarantee in favor of the Board from a Bank approved by the Engineer, as surety…….................................................. ...............................………………..………………………………..(Rs.............……....) which said Performance Guarantee shall remain in force and shall not be discharged until the Engineer shall have granted a Final Certificate to the effect that the Contractor has duly discharged and completed all his obligations under this contract and that there is no sum whatever due to the Board at the date of such Final Acceptance Certificate under this Contract.

5.	The following terms used in this Agreement and or in the Specifications shall be understood as having the meanings hereby ascribed to them, namely;

"The Procurement Committee" shall mean the Procurement Committee appointed for the purpose of determining the Tender.

"The Contractor" or "The Supplier" shall mean the person or persons, firm or firms, company or companies who have contracted for the supply and delivery of the materials, equipment and installation herein specified and includes its successors and permitted assigns.

"The Chairman" shall mean the officer for the time being holding the office of or acting as the Chairman, National Water Supply and Drainage Board.

"The Engineer" shall mean the Officer for the time being holding the Office of or acting to the General Manager, National Water Supply and Drainage Board.

"The Engineer's Representative" shall mean the authorized Representative of the Engineer immediately responsible for the supervision of the Works or any other person appointed from time to time by the Engineer to act as Engineer and notified in writing to the Contractor.

"The Government" shall mean the Government of the Democratic Socialist Republic of Sri Lanka.

"The Purchaser" or "The Board" shall mean the National Water Supply and Drainage Board.

"Months" shall mean calendar months.

"The Contract Documents" shall mean the Instructions to Bidders, Contract Data, Bidding Data, Schedule of Particulars, the General Conditions of Contract, the Form of Bid, the Specifications, Bill of Quantities, Addenda, Articles of Agreement and their annexure.

"The Contract Price" shall mean the sum stated in the Letter of Acceptance payable to the Contractor for the supply of Goods and Services in accordance with the provisions of the Contract.

"The Works" shall mean the supply, delivery and Installation of Goods and the Services.

"Variation" shall mean any alteration of the description of any item in the Bill of Quantities or of the Specifications which in the opinion of the Engineer, is required for the perfect completion of the Works outlined in the Agreement.

"RS or SL Rs." shall mean Sri Lanka Rupees.

IN WITNESS WHEREOF the parties hereto have set their hands and seal to these presents at the places and dates hereinafter mentioned.

Signed by the said ..............................................................…………. Chairman, National Water Supply and Drainage Board and…………………… ... Board Member of the National Water Supply and Drainage Board at ………………………......................……………… on the ............................................... day..................…………........………….……….……………….. of………………..………................................Two Thousand and ………………………….. …….……………….in the presence of the following Witnesses.

Chairman ...................…….................	Board Member ....................…

NATIONAL WATER SUPPLY AND DRAINAGE BOARD

WITNESSES

Signature 1:	….………........................	Signature 2 : ........................

Name	        :…………………………….	Name		:…………………..

Address	...........................……....	Address	:………………

……………………….			……………………….

Signed by the said .......................................................................... in the capacity of .............................................at..................................on the ………………........ day of.........………………... Two Thousand and ............. in the presence of the following Witnesses.

……................................

Signature of Contractor

WITNESSES

Signature 1:	.....................……..	Signature 2 :.……….....................

Name	      :	……………………… Name	        : …..……………………

Address	.................................	 Address	................................

.................................			................................

Capacity     ………………………....  Capacity     ………………………....

FORM OF PERFORMANCE SECURITY (Unconditional)

…………………………..[Issuing Agency’s Name and Address of issuing Branch or Office]

…………………………..

…………………………..

Beneficiary: Chairman

National Water Supply and Drainage Board

Galle Road, Ratmalana

Date ……………..

PERFORMANCE GUARANTEE No.: …………………………………………………..

We have been informed that …………………………………………………………….. [name of Contractor/Supplier] (hereinafter called “the Contractor”) has entered into Contract No. …………………….. dated ……………….  with you, for the Supply & installation of ………………………………………………………………………………….. [name of contract and brief description of Works] (hereinafter called “the Contract”).

Furthermore, we understand that according to the conditions of the Contract, a performance guarantee is required.

At the request of the Contractor, we ………………………………………… [name of Agency] hereby irrevocably under take to pay you any sum or sums not exceeding in total and amount of ………………… [in figures] ………………………………………  ………… [in words], such sum being payable in the types and proportions of currencies in which the Contract Price is payable, upon receipt by us of your first demand in writing accompanied by a written statement stating that the Contractor is in breach of its obligation (s) under the Contract, without your needing to prove or to show grounds for your demand or the sums specified therein.

This shall expire, no later than the ……………… day of ………………… , 20 …………… [28 Days beyond the Defects Liability Period] and any demand for payments under it must be received by us at this office on or before that date.

………………………………………………….

[Signature (s)]

Signature and seal of the guarantor

Witness

Name	:      ………………………………………………………………

Signature : ………………………………………………………………

Revised on 22-05-2019

………………………………

………………………………

………………………………

………..-20….

Regd. Post

Ms. ……………………………………….

……………………………………………

……………………………………………

Dear Sirs,

SUPPLY & INSTALLATION OF ………………………………………………………..

……………… PUMPS AND ACCESSORIES

### CONTRACT NO: …………………………………..

Letter of Acceptance

We are pleased to inform you that your offer submitted on …………………… on the above tender, amounting to Sri Lanka Rupees ………………………………………. (LKR ……………………../=) has been accepted.

- Applicable VAT will be payable on production of Tax Invoices.  The Registered No. for NWSDB for VAT is 4090318207000.

### …………………………………………………………….  Pumps & Accessories should be from …………………………………

Inspection and Testing of goods should be carried as per Clause 25 of General Conditions of Contract with respect to quantity, quality and loading prior to shipment and certificates should be forwarded to Deputy General manager (…………….)

All Pumps & Accessories under this contract shall be delivered at such places, in such quantities as specified in the Delivery Schedule and Contract Period is ……………………… months from the date hereof.

The liquidated damages for any delay beyond the above period shall be LKR ………….... ../=  per Day not exceeding 10% of the total Contract Price.

An advance payment shall not be paid for this contract.

Performance Security in the form of demand guarantee in the prescribed format (a copy annexed) from a recognized bank operating in Sri Lanka approved by the Central Bank of Sri Lanka for an amount of 10% of the total Contract Price valid for a period of 28 Days beyond the Defects Liability Period, from the date hereof shall be submitted within 14 Days from the date hereof. Performance Security shall be denominated in the currency of contract and proportionate to each currency.

Revised on 17-06-2024

Please acknowledge receipt of this letter by a return fax and make arrangements to sign the Agreement by prior appointment with the Asst. General Manager (Tenders & Contracts) within 28 Days.

Engineer’s Representative of this contract is …………………………………..

Please contact Deputy General Manager (………………..) on Tele No. …………….. for further action on this contract.

Yours faithfully,

National Water Supply & Drainage Board

General Manager

Cc:	1.	Secretary, Ministry of  ………………………………………………..

- Auditor General – Duplicate offer and a copy of the Tender Board decision attached.

- Addl. General Manager (…………)

- Deputy General Manager (…………)

- Deputy General Manager (Finance)

- Deputy General Manager (IA)

- Asst. General Manager (……………)

- Chief Engineer (…………………….)

- Stores Copy

Revised on 10-11-2020

Revised on 22-05-2019

.

12.  APPENDICES

APPENDIX 1A- DETAILS OF SIMILAR SUPPLIES COMPLETED WITHIN THE LAST FIVE YEARS AND ONGOING

| Name and Address of Employer | Name and details of Contract | Value of Contract | Period of Contract Date |  | Remarks (Completed/ ongoing etc) | Value of work remaining incomplete |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | From | To |  |  |

APPENDIX 1B -DETAILS OF SIMILAR INSTALLATION COMPLETED WITHIN THE LAST FIVE YEARS AND ONGOING

| Name and Address of Employer | Name and details of Contract | Value of Contract | Period of Contract Date |  | Remarks (Completed/ ongoing etc) | Value of work remaining incomplete |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | From | To |  |  |

APPENDIX 2 - Schedule of  Technical persons & facilities

1.  Details of Workshops

| Location | Minimum Facilities Required | Available facilities | Remarks |
| --- | --- | --- | --- |
|  | - General Engineering tools - Hydraulic pressure - Precision measuring tools - Power factor - Clipon meter - Power analyzer - Flow meter - Pressure gauges - Motor starters - Meggar |  |  |

2.   Stocks of Spare Parts

| Item | Minimum No required | Availability | Remarks |
| --- | --- | --- | --- |
| Bearings |  |  |  |
| Packings |  |  |  |
| Circlips & similar specials fasteners |  |  |  |
| Lantern rings |  |  |  |
| Wear rings |  |  |  |

Technical Staff

Mechanical Engineer /or 	01

Electrical Engineer 		01

Technical officer

(Mechanical/Electrical)	01

Mechanic			01

Electrician 			01

APPENDIX  3  -  FINANCIAL STATEMENT

Summary of assets and liabilities based on the audited financial statements for the last three financial years (Current statement may be unaudited) together with the Financial Performance as indicated in the following schedule shall be submitted.

If the business has not been in operation for three years following schedule shall be submitted for the period that the business has been in operation together with the aforesaid financial statements.

Bidders whose financial capability is marginally less to undertake this bid may show credit facilities available to them from a Banks.

# Financial performance for the last 3 years

| Year | xxxx | xxxx | xxxx |
| --- | --- | --- | --- |
| Turnover from Contracting |  |  |  |
| Fixed Assets (FA) |  |  |  |
| Current Assets (CA) |  |  |  |
| Current Liabilities (CL) |  |  |  |
| Long Term Liabilities (LL) |  |  |  |
| Net Worth =Total Assets – Total Liabilities |  |  |  |
| Current Ratio = Current Assets Current Liability |  |  |  |
| Liquidity Ratio = Current Assets(except stock) Current Liability |  |  |  |
| Gearing Ratio = Debt Capital x 100 Total Capital Employed |  |  |  |
| Turnover x 100 Total Operating Assets |  |  |  |
| Net Profit x 100 Total Assets |  |  |  |

# APPENDIX 3A – AUTHORIZATION FOR BANK REFERENCES

BIDDER SHALL FILL THIS FORM AND PROVIDE WITH THE BID

…….………… [Bidder’s Name]

………………….........[Address]

………………………………….

..……………………………….

Manager …………………….. [Name of Bank]

………………..……………….[Address]

…………………………………………

…………………………………………

Dear Sir,

I hereby Authorize the National Water Supply & Drainage Board, on behalf of the Procurement Committee, to seek references of Bank details in order to  evaluate the financial statues  of  our company M/s ……………………………………………………………………

…………………………………………………….…………………….[Bidder’s Name & Address]  in connections with the ……………………………………………………… [Contract Name & Number] bid, submitted by us.

Yours faithfully,

………………………………..

………………………………..

Authorized officer of the Bidder.

Note : 	If there are more than one bank, separate letters should be submitted for each Bank.

Revised on 24-12-2021

Appendix 4 - Confirmation of Capability of Production and

Supply according to Delivery Schedule.

[Address of the Manufacturer]

…………………………………………..

………………………………………….

………………………………………….

Chairman,

Procurement Committee,

# Supply & Installation of ………………… Sewage Pumping Sets and Accessories

………………………… Sewerage Scheme

Contract No…………………………………….

We, ……………………………………………………………….[name of manufacturer] of…..………………………………………………………………………………………………………………………………………………..…….[address of  manufacturer]confirm that we have sufficient production capacity to produce the quantity of  Pumps and Accessories submitted in our bid and shall deliver them according to the delivery schedule indicated in the bid.

……………………………..					……………………………..

Authorised Officer of the Manufacturer.			   Seal of the Company.

Name:  ……………………………..

Certified by

…………………………………..                                              ……………………………                          Authorized officer of the Bidder                                                     Seal of the Company

Name :……………………………..

Revised on 22-03-2023

Appendix 5 -  Manufacturer’s Authorization to sign the

Contract

[The Bidder shall require the Manufacturer to fill in this Form in accordance with the instructions indicated. This letter of authorization should be on the letter head of the Manufacturer and should be signed by a person with the proper authority to sign documents that are binding on the Manufacturer. The bidder shall include it in its bid].

Date : [insert date (as day, month and year) of Bid Submission]

No. : [insert contract number]

To :  Chairman,

Procurement Committee,

# Supply & Installation of ………………… Sewage Pumping Sets and Accessories

………………………… Sewerage Scheme

Contract No…………………………………….

We …………………………………………[insert complete name of  Manufacturer], who are official manufacturers of Sewage Pumping sets and accessories,  having factories at ……………………………………….…………[insert full address of Manufacturer’s factories], do hereby authorize …………….………………………….. [insert complete name of  Bidder] to submit a bid the purpose of which is to provide, Sewage Pumping sets and accessories  manufactured by us …………………………………….. [insert name] and to subsequently negotiate and sign the Contract.

We hereby extend our full guarantee and warranty in accordance with Clause 27 of the General Conditions of Contract, with respect to the Goods offered by the above firm.

Signed :  …………………………………[insert signature(s) of authorized representative(s) of the Manufacturer]

Name : ………………………………………………………..[insert complete name(s) of authorized representative(s) of the Manufacturer]

Title :  …………………………………….. [insert title]

Duly authorized to sign this Authorization on behalf of :  ……………………………[insert complete name of  Bidder]

Dated on  …………………….. day of  …………………………….[insert date of signing].

Revised on 22-05-2019

APPENDIX 6 -   SCHEDULE OF PLANT AND EQUIPMENT PROPOSED

FOR PUMPS, INSTALLATIONS

Note:

1.	The categories indicated below are only the minimum requirement proposed by NWSDB for information.  The Bidder should declare the actual plant and equipment that he proposes to use for the execution of the works. These plant and equipment should be in usage for not more than five years after their first purchase/use.

| Item | Description | Minimum No. Proposed by NWSDB | Minimum No. Provide by the contractor | Minimum Period Proposed | Remarks (hired/own) |
| --- | --- | --- | --- | --- | --- |
|  | Mechanical |  |  |  |  |
| 1 | Dial gauge |  |  |  |  |
| 2. | Complete tool box |  |  |  |  |
| 3. | Allen Key set (Standard sizes) |  |  |  |  |
| 4. | Hand Roller 2 – 3 ton |  |  |  |  |
| 5. | Disc Grinding machine |  |  |  |  |
| 6. | Drilling machine (Both steel and concrete) |  |  |  |  |
| 7. | Welding Plant (Arc) |  |  |  |  |
| 8. | Gas Welding Plant (Oxy Estelline) |  |  |  |  |
| 9. | 3 Jaw Puller |  |  |  |  |

| Item | Description | Minimum No. Proposed by NWSDB | Minimum No. Provide by the contractor | Minimum Period Proposed | Remarks (hired/own) |
| --- | --- | --- | --- | --- | --- |
| 10 | Grease gun |  |  |  |  |
| 11. | Vernier, micro screw gauge, outside/inside caliper |  |  |  |  |
| 12 | Measuring tape (steel) |  |  |  |  |
| 13 | Level gauge |  |  |  |  |
| 14 | Slip gauge |  |  |  |  |
| 15. | General Pliers, Nose pliers, hammer etc |  |  |  |  |
| 16. | Tripod |  |  |  |  |
| 17 | Mobile Crane (up to 5 tons) |  |  |  |  |
| 18. | Air Compressor with all painting accessories. |  |  |  |  |
| 19. | Decibel meter |  |  |  |  |
| 20 | Vibration pen |  |  |  |  |
| 21. | Thermo meter |  |  |  |  |
| 22. | Tacho meter |  |  |  |  |
| 23 | Filing set |  |  |  |  |
| 24. | Safety Equipments when handling chemicals and others |  |  |  |  |

| Item | Description | Minimum No. Proposed by NWSDB | Minimum No. Provide by the contractor | Minimum Period Proposed | Remarks (hired/own) |
| --- | --- | --- | --- | --- | --- |
|  | Electrical |  |  |  |  |
| 25. | Clip-on meter |  |  |  |  |
| 26. | Power analyzer |  |  |  |  |
| 27. | Hydraulic Crimping tool |  |  |  |  |
| 28. | Single Phase up to 5 KVA Generators. |  |  |  |  |
| 29. | Three phase 5 – 50 KVA Generators. |  |  |  |  |
| 30 | Three Phase 50 – 100 KVA Generators. |  |  |  |  |
| 31 | Three Phase 100 – 200 KVA Generators. |  |  |  |  |
| 32. | Necessary instruments & items for site lighting. |  |  |  |  |
| 33. | Insulation resistance tester |  |  |  |  |
| 34. | Earth resistance tester |  |  |  |  |

Appendix 7 - BIDDER’s Authorization to sign the Contract

[The Bidder shall require to fill in this Form in accordance with the instructions indicated. This letter of authorization should be on the letter head of the Bidder and should be signed by a person with the proper authority to sign documents that are binding on the Bidder. The bidder shall include it in its bid].

Date : [insert date (as day, month and year) of Bid Submission]

No. : [insert contract number]

To :  Chairman,

Procurement Committee,

………………………….

………………………….

# Supply & Installation of ………………… Sewage Pumping Sets and Accessories

………………………… Sewerage Scheme

Contract No……………………………………

We …………………………………………[insert complete name of  the Bidder], who ……………………………………….…………[insert full address of Bidder], do hereby authorize …………….………………………….. [insert complete name of  Bidders authorize officer who signs the contract] to submit a bid on behalf of our company and to subsequently negotiate and sign the Contract.  We will supply the goods as per the Contract.

Specimen Signature …………………………………………………………

Signed :  …………………………………[insert signature(s) of authorized representative(s) of the Bidder]

Name : ………………………………………………………..[insert complete name(s) of authorized representative(s) of the Bidder]

Title :  …………………………………….. [insert title]

Duly authorized to sign this Authorization on behalf of :  ……………………………[insert complete name of  Bidder]

This is to certify that the seal and signatures of legal representative and authorized person affixed to power of attorney attached hereto are found to be authentic.

………………………………

Signature of Attorney at Law

……………………………..

Seal of Attorney at Law

In the place of  (…………………………………………………………………………….. address)

Date ……………………

Appendix 8 - TOR for the Independent Inspection Agency

Inspection of Pump MOtOr Assemblies

|  | Test | Measurement Value / Observation Comments |
| --- | --- | --- |
| 01. | Visual Tests Casting , Machining, Welding , Dimensions, finish data like fillets, corners etc. Surface finish, surface preparation, painting. Alignment of the whole assembly. |  |
| 02. | Test Set – up / facilities Suitability of the factory test set – up for the specified pump tests. Suitability of the instrumentation for measurements, data transfer / storage / processing ,report generation, including acceptable calibration. |  |
| 03. | Status of the tested equipment, whole set –up, Instrumentation etc after running for an adequate time stabilization. Temperature at various points. noises Vibrations Leakages Distortions Cavitations Others |  |
| 04. | Measurements ( General) Voltage Currant Power Power Factor Insulation Resistance (others specific to the particular contract) |  |

|  | Test | Measurement Value / Observation Comments |
| --- | --- | --- |
| 05. | Operational Measurements Flow rate Delivery pressure Suction pressure Power drawn by motor |  |
| 06. | Hydrostatic Test For pumps between 20 – 75 kw. Test the components at 150% of the pump shut off head for 10 minutes. For pumps larger than 75 kw. Test the components at 150% of the pump shut off head for 30 minutes. |  |

APPENDIX  9 -  Manufacturer’s awareness of the TOR for

Independent Inspection Agency AND CHECKLIST

FOR PRE-SHIPMENT INSPECTIONS

[Address of the Manufacturer]

…………………………………………..

………………………………………….

………………………………………….

Chairman,

Procurement Committee,

# Supply & Installation of ………………… Sewage Pumping Sets and Accessories

………………………… Sewerage Scheme

Contract No…………………………………….

We, ……………………………………………………………….[name of manufacturer] of ………………………………………………………………………………………………………………….………………………………………………………………..…….[address of  manufacturer]confirm that we have noticed that

a)   Appendix   8 – TOR for Independent Inspection Agency

c)   Clause 25.6 of   Instructions to Bidders.

…………………………………………			    ..…………….………

Authorised Officer of the Manufacturer.			   Seal of the Company.

Name :……………………………………

Certified by

…………………………………..                                              ……………………………                          Authorized officer of the Bidder                                                     Seal of the Company

Name :……………………………..

Revised on 22-03-2023

APPENDIX 10 - Manufacturer’s Warranty for the goods (supplied

under the contract)

[Address of the Manufacturer]

…………………………………………..

………………………………………….

………………………………………….

Chairman,

National Water Supply and Drainage Board,

Galle Road, Ratmalana, Sri Lanka,

# Supply & Installation of ………………… Sewage Pumping Sets and Accessories

………………………… Sewerage Scheme

Contract No…………………………………….

We, ……………………………………………………………….[name of manufacturer] of ……………………………………………………..…….[address of  manufacturer]warrant that the goods supplied under this contract are new, unused, of the most recent or current models and have incorporated all recent improvements, and no defects arising out of the design, material or workmanship from any act that may be develop under normal use of the supplied goods.

If there is any defects during the warranty period specified in the Clause 27 of the General Conditions of Contract, we shall attend to repair or replace the defective goods with all reasonable speed without any cost to the Purchaser.

Also we enclose further details in the given table below.

| Part/ Section | Warranty period |
| --- | --- |

…………………………………………			    ..…………….………

Authorised Officer of the Manufacturer.			   Seal of the Company.

Name :……………………………………

Certified by

…………………………………..                                              ……………………………                          Authorized officer of the Bidder                                                     Seal of the Company

Name :……………………………………

Revised on 22-03-2023

APPENDIX  11–  PRE-SHIPMENT Inspection of Pump AND Motor

Assemblies BY TEAM OF NWSDB Engineers

|  | Test/Activity | Measurement Value/Observations & Comments |
| --- | --- | --- |
| 01 | Visual Tests Comments on castings Comments on machining Comments on welding, fillets, corners and similar features Comments on surface finish and painting Comments all drillings, positioning etc. Comments on assembly |  |
| 02 | Operational status of the equipment under test ( after operation until stabilisation) Observation on temperature at various points Observations on excessive noise emissions Observations on excessive shaking or vibration Observations on excessive leakages Observations of any distortions of parts Observations of possible cavitation Observations on the measuring equipment |  |

|  | Test/Activity | Measurement Value/Observations & Comments |
| --- | --- | --- |
| 03 | Measurements (General) Voltage Current Power Power factor Insulation resistance |  |
| 04 | Operational Measurements Flow rate Delivery pressure Suction pressure Power drawn by motor |  |
| 05 | Hydrostatic Test For pumps between 20 – 75 kw. Test the components at 150% of the pump shut off head for 10 minutes. For pumps larger than 75 kw. Test the components at 150% of the pump shut off head for 30 minutes. |  |

APPENDIX  12 -	Guidelines for the acceptance of pump

and Motor Assembles at NWSDB  sites BY

INSPECTION TEAM

|  | Activity / Test | Measurements / Value / observation Comments. |
| --- | --- | --- |
| 01. | Preparation of list of finalised and agreed list of parameters, delivery scope, submittals etc. of parameters, after PC –Procurement Committee approval, any subsequent amendments. |  |
| 02. | Manufacturer Country of Origin Make Model Delivery of Test reports ( 3rd party / Manuf./ client.) |  |
| 03. | Compliance of the whole delivery scope with finalised client’s requirements. |  |
| 04. | Compliance of the specification of equipment , spare , tools, submittals etc. |  |
| 05. | Compliance of the installation with the manufacturer’s recommendations. |  |
| 06. 07. | Compliance of the test instruments with properly carried out calibration. Suitability of the instrumentation for measurement , logging , processing etc of the test data with regard to range, accuracy, least count etc. |  |
| 08. | Observation of the whole set-up after running the assembly until stabilisation. |  |

|  | Activity / Test | Measurements / Value / observation Comments. |
| --- | --- | --- |
| 09. | Get the measurements for 05 operating points. 1. Shut off 2. Oper. Point 3. Max. recommended Point 4. a point between (1) & (2) above 5. a point between (2) & (3) above - Currant - Voltage - Power drawn by motor - Flow rate - Suction pressure - Delivery pressure |  |
| 10. | Tabulate measurements , calculations Flow rate Pressure Power drawn by pump Power drawn by motor Pump efficiency Overall efficiency ( any other particular to this contract) |  |
| 11. | Any deviations of the test results from the submitted test reports (3rd party / manuf./ client) |  |
| 12. | Observations / Comments on the deviations. |  |
| 13. | Acceptance / rejection of the equipment with justifications. |  |

APPENDIX 13 – AFFIDAVIT BY THE BIDDEER

I ………………………………………… of ………………………………………… being a ……………………… (Buddhist or any other religionist), do hereby solemnly sincerely and truly declare and affirm as follows.

01.	I am the Affirmant above named.

02.	I hereby declare that I have applied for the contract of National Water Supply and Drainage Board bearing No: …………………………………….. and my spouse or dependent does not work in National Water Supply and Drainage Board on permanent, casual or contract basis.

The foregoing affidavit having been read over and explained to the affirmant above named who having understood its nature content and context affirmed hereto and set his usual signature hereto in ……………...     on this ………….……………… day of …………….…….. 20……….

Before me	           ……………………

Declarant

…………………………………

Justice of the Peace /

Commissioner for oaths

APPENDIX  14  -  ENTITLED ALLOWANCES ON FOREIGN TRAVELS &

RELATED EXPENSES