## cal 1
90 mm dia P.V.C
Drawing No | Pipe Length | Bend |  |  |  | washout | Air valve | Culvert Type
|  | 111/4 | 221/2 | 45 | 90 |  |  | 1 | 2 | 1 | 2
1 | 497.56 |  | 2 | 2 |  | 1 | 1 |  | 1200 |  | 3000
2 | 212.2
3 | 677.91 |  | 2 | 1 |  | 1
4 | 428 |  | 1 |  |  | 1 | 1 |  | 1200 |  | 3000
5 | 436.01 |  |  |  |  | 1 |  | 1000 |  | 2800
6 | 551.8 |  | 4 | 2 |  | 1 |  | 600 |  | 2400
[8 empty] | 600 |  | 2400
[8 empty] | 630 |  | 2430
7 | 499.01 |  | 7 | 1 | 1 | 1 | 1 |  | 1450 |  | 3250
8 | 366.37 |  | 3 |  |  |  |  | 2100 |  | 3900
| 228.69 |  | 3 | 3 |  |  |  | 600 |  | 2400
9 | 433.41 |  | 6 | 1 |  | 1 | 1
10 | 89.11
| 144.49 |  | 1
11 | 326.73 |  | 1
| 196.01 |  | 2 | 1 |  | 1
12 | 172.52 |  | 1
232.23
13 | 141.49 |  | 1
268.47
14 | 137.8 |  | 5 | 1
16 | 335.19 |  | 1 |  |  | 1 | 1 | 600 |  | 2400
17 | 23.68 |  |  |  | 1 |  | 1
18 | 750 |  | 8 | 1 | 2 | 1 |  |  |  |  | 3000
19 | 90.8 |  | 1 |  |  | 1
24 | 694.06 |  | 4 | 5 | 1 | 1 | 1
25 | 225.59 |  |  |  |  | 1
26 | 163.05
27 | 229.08 |  | 2
28 | 319.66 |  | 1 | 1 |  | 1 | 1
29 | 198.62 |  | 1 |  | 1
30 | 320.48 |  | 1
32 | 444.82 |  | 1 |  |  |  | 1
33 | 120.4 |  | 1 |  | 1
34 | 525.11 |  | 4 | 9 | 2 | 1 | 1 | 1800 |  | 3600
35 | 239 |  |  |  | 1
36 | 711.25 |  | 4 | 2 |  | 1 | 1 |  | 2750 |  | 4550
37 | 631.11 |  | 1 | 1 |  | 1 | 2
38 | 453.36 |  | 1 | 2 | 3
39 | 467.7 |  |  | 2 | 2 | 1
40 | 312.16 |  |  |  | 1
41 | 477.2 |  | 1 |  | 4 | 1 | 1
42 | 271.6 |  |  |  | 3
44 | 198.34 |  | 3 | 1 |  | 1
45 | 535.88 |  |  | 2 | 6 | 1 | 1
46 | 358.45 |  | 4 |  | 2 | 1 | 1
47 | 750 |  | 2 | 2 |  | 1 |  | 1700 |  | 3500
[8 empty] | 600 |  | 2400
[8 empty] | 2000 |  | 3800
48 | 371.85 | [5 empty] | 1
49 | 375.39 |  |  |  |  | 1 | 1
50 | 292.05 |  | 1 |  | 1
51 | 384.13
52 | 167.49 |  | 3 | 2 | 1 | 2
53 | 425.96 |  | 6 | 1 |  | 2
55 | 76.19 |  |  |  | 1
57 | 285.54 |  | 1 |  | 2
58 | 667.72 |  |  |  | 2 | 1 | 1 | 1200 |  | 3000
61 | 582.65 |  | 1 |  | 1 |  | 1 |  | 900 |  | 2700
62 | 541.77 |  |  |  |  | 1
63 | 593.78 |  | 4 |  |  |  | 1
64 | 281.66 |  |  |  |  | 1 |  | 1300 |  | 3100
65 | 617.75 |  | 1 |  | 1 | 1 | 1 | 900 |  | 2700
[8 empty] | 600 |  | 2400
66 | 135.35
67 | 507.79 |  |  | 1 |  | 1 | 1
68 | 665.96 |  | 7 | 3 |  | 1 | 1
69 | 428.72 |  |  | 3 |  | 1 | 1
70 | 452.59 |  | 2 | 2
71 | 553.08
72 | 416.39 |  | 4 | 1 |  |  | 1 | 1400 | 2300 | 3200
73 | 336.09 |  | 5 | 2
74 | 341.34 |  | 3 | 1
75 | 270.06 |  | 1
76 | 312.3 |  | 1 | 2
77 | 291.12 |  | 1 | 1
78 | 491.88
81 | 510.85 |  |  |  |  | 1
82 | 536.35 |  |  |  |  | 1 |  | 600 |  | 2400
83 | 140.92 |  |  | 1 |  | 1
86 | 513.31 |  | 2 |  |  |  |  | 1300 |  | 3100
[8 empty] | 1150 |  | 2950
87 | 750.48 |  |  |  |  | 1 | 2 |  | 900 |  | 2700
88 | 752.48 |  |  |  |  | 1 |  | 1300 | 3600 |  | 5400
89 | 749.14 |  | 6 |  |  | 1 | 1 | 600 |  | 2400
[8 empty] | 800 |  | 2600
90 | 521.57 | [6 empty] | 800 |  | 2600
91 | 308.72
92 | 323.28
93 | 496.68 |  | 4 | 2 |  | 1
94 | 748.61 |  | 4 | 4 |  | 1 | 1
97 | 182.33 |  | 1 | 1
100 | 432.47 |  | 1 |  | 1 |  |  |  | 900 |  | 0
102 | 233.22 |  | 4
105 | 493.7 |  |  |  |  | 1
106 | 490.77 |  | 6 |  |  | 2 |  | 2400 | 4200
| 34937.88 |  | 149 | 67 | 41 | 46 | 30 |  |  | 62480 | 27600

## Cal 2
110 mm dia. (P.V.C)
Drawing No | Pipe Length | Bend |  |  |  | washout | Air valve | Culvert Type
|  | 111/4 | 221/2 | 45 | 90 |  |  | 1 | 2 | 1 | 2
1 | 250.08 |  |  |  |  | 1 |  | 600 |  | 2400
2 | 537.78 | [5 empty] | 1
10 | 27.02
16 | 414.94 |  | 3 |  |  |  |  | 900 |  | 2700
17 | 726.61
21 | 90.56 |  | 1 | 1 |  | 1
23 | 552.47 |  | 4 |  |  | 1 | 1 |  | 900 |  | 2700
25 | 68.71 |  | 2
30 | 137.25
32 | 187.35 |  | 1
43 | 209.69 |  | 1
44 | 162.12
54 | 630 |  | 6 | 1 |  | 1 |  | 1300 |  | 3100
55 | 441.97 |  | 3 | 2 |  | 1 | 1 |  | 1000 | 2800
58 | 81.83
59 | 748.66 |  | 1 | 1 |  |  | 1
60 | 320.83 |  | 1 | 1 |  | 1 |  |  | 900 |  | 2700
| 216.91 | [5 empty] | 1
61 | 167.23 |  |  |  |  | 1 |  |  | 3000 |  | 4800
63 | 154.41
66 | 367.48 |  |  |  |  | 1 | 1
79 | 750 |  |  |  | 1 |  | 1 |  | 900 |  | 2700
[9 empty] | 1300 | 3100
80 | 86.13 | [7 empty] | 3000 |  | 4800
84 | 734.97 |  | 14 | 8 | 2 | 1 | 1
85 | 748.8 |  |  |  | 2 |  |  | 600 | 1200 | 2400 | 3000
92 | 25.38
95 | 750 |  |  |  | 1 |  |  | 800 |  | 2600
96 | 653.82 |  | 7 | 7 | 6 | 1 |  | 450 |  | 2250
[8 empty] | 600 |  | 2400
97 | 426.02 |  | 4 | 2 | 1 | 1
98 | 609.21 |  | 5 | 1 |  | 1 | 1 | 450 |  | 2250
99 | 463.35 |  |  | 2 | 2 | 1 |  |  | 900 |  | 2700
101 | 155.92 |  |  |  |  | 1 |  | 900 |  | 2700
102 | 240 |  | 1 |  |  |  |  | 600 |  | 2400
103 | 589.2 |  | 11 | 5 | 1 | 1 | 1
104 | 653.35 |  | 4 |  |  | 1 | 1 |  | 1000 |  | 2800
[9 empty] | 1200 |  | 3000
| 13380.05 |  | 69 | 31 | 16 | 16 | 11 |  |  | 28700 | 29200 | 13380.05

## cal3
160 mm dia. P.V.C
Drawing No | Pipe Length | Bend |  |  |  | washout | Air valve | Culvert Type
|  | 111/4 | 221/2 | 45 | 90 |  |  | 1 | 2 | Bidge crossing | 1 | 2
4 | 321.17 |  |  |  |  | 1 |  | 600 |  |  | 2400
5 | 313.83 |  | 1
9 | 25
15 | 715.97 |  | 2 |  |  |  | 1
20 | 443.52 |  |  |  |  | 1 | 1
21 | 611.85 |  | 6 | 1 |  |  | 1 |  | 2000 |  |  | 3800
22 | 438.03 |  | 1 |  |  | 1 |  | 1400 |  |  | 3200
30 | 292.27 |  | 2
31 | 750 |  | 7 |  |  | 1 | 1 |  | 2500 |  |  | 4300
[6 empty] | 1 |  |  | 2100 |  |  | 3900
32 | 117.83
43 | 540.31 |  | 2 | 2 |  | 1 | 1 | 1200 | 1800 |  | 3000 | 3600
52 | 198.82 |  | 1 | 2 | 1 |  |  |  |  | 1
54 | 120 |  | 1
56 | 327.34 |  | 1 | 2 | 1 |  |  |  |  | 1
60 | 213.18 | [6 empty] | 1300 |  |  | 3100
101 | 607.56 |  | 9 | 7 |  | 1 | 1 |  | 3000 |  |  | 4800
| 6036.68 |  | 33 | 14 | 2 | 7 | 6 |  |  |  | 11700 | 20400

## cal4
225 mm dia. P.V.C
Drawing No | Pipe Length | Bend |  |  |  | washout | 25 mm dia. Air valve | Culvert Type
|  | 111/4 | 221/2 | 45 | 90 | 80dia. |  | 1 | 2 | 3
20 | 300
20 | 300

## Junction
JUNCTION DETAIL
Juntion Nr. | 110mm P.V.C pipe (m) | 90mm P.V.C pipe (m) | 160mm P.V.C pipe (m) | 160mm P.V.C socketed 90 bend | 90mm P.V.C socketed 90 bend | 110mm P.V.C socketed 90 bend | 100mm Flanged and Plain ended D.I pipe 1.0m | 100mm Flanged D.I pipe 0.5m | 450 x 100 D.I socketed tee with flanged branch | 450 x 150 D.I socketed tee with flanged branch | 90 x 90 mm P.V.C tee | 110x110tee | 110 x 90 tee | 160 x160 mm P.V.C tee | 160 x 110 mm tee | 160 x 90 mm tee | 200-100 mm D.I Flanged reducer | 150 - 100 mm D.I flanged reduser | 160 -110 reduser | 160-90 mm reduser | 110 -90mm .reduser | 90 -63mm .reduser | 225-160mm .reduser | 100 mm dia. Pressure redusing valve | 100 mm meter | 80mm dia. SV | 100 mm dia. SV | 150 mm dia. SV | 90 mm dia end cap | 110 mm dia end cap | 160 mm dia end cap | 200 V.J.F.A | 150 V.J.F.A | 100 mm V.J.F.A | 80 mm V.J.F.A | 100 mm dia. Flexible mecanical coupling
1 | 8 | 1 |  |  |  | 2 | 2 | 1 | [5 empty] | 1 |  |  |  | 1 | 1 | 1 | 1 |  |  | 1 | 1 | 1 | 2 | 1 |  |  |  |  | 2 | 1 | 2 | 1
2 | 4 | 5 | 10 | [8 empty] | 1 |  | 3 |  | 1 |  |  | 2 | 1 | [5 empty] | 3 | 2 | 2 |  |  |  |  | 4 | 4 | 6
3,4,33 |  | 3 | 3 | [12 empty] | 3 | [9 empty] | 3 |  | 3 |  |  |  |  | 2 |  | 6
5 |  | 1 | [8 empty] | 1 | [14 empty] | 2 | [8 empty] | 4
6 |  | 3 | [8 empty] | 1 | [14 empty] | 2 | [8 empty] | 4
7 |  | 2 | [8 empty] | 1 | [14 empty] | 2 | [8 empty] | 4
8 |  | 3 | [8 empty] | 1 | [9 empty] | 1 |  |  |  |  | 2 | [8 empty] | 4
9,10 |  | 4 | [8 empty] | 2 | [14 empty] | 4 | [8 empty] | 8
11,13 | [10 empty] | 2 | [14 empty] | 2 | [8 empty] | 4
12 |  | 2 | [8 empty] | 1 | [14 empty] | 2 | [8 empty] | 4
15 | [20 empty] | 1
16 | [26 empty] | 1 | [6 empty] | 2
14/17/18/ | [28 empty] | 16
34 |  | 3.4 | [8 empty] | 1 | [17 empty] | 1
32 | [30 empty] | 1
35,36 |  | 2 | [8 empty] | 1 | [17 empty] | 2
2//1 | [10 empty] | 1 | [14 empty] | 1 | [8 empty] | 2
2 |  | 3 | [8 empty] | 1 | [9 empty] | 1 |  |  |  |  | 2 | [8 empty] | 4
3 | [11 empty] | 1 | [14 empty] | 1 | [6 empty] | 2
4 | 2 | [11 empty] | 1 | [12 empty] | 1 | 1 | [6 empty] | 2 | 2
5 | 18 |  |  |  |  | 1 | 2 | 1 | 1 |  |  | 2 |  |  |  |  | 1 | 1 | [5 empty] | 1 | 1 |  | 4 |  |  |  |  | 1 |  | 6 |  | 2
6,17 | 4 | [11 empty] | 2 | [12 empty] | 2 | 2 | [6 empty] | 4 | 4
7 |  | 1 |  |  |  | 1 | [14 empty] | 1 |  |  |  |  | 1 | [8 empty] | 2
8 | 2 | [9 empty] | 1 | [14 empty] | 2 | [8 empty] | 4
9 | 3 |  | 5 | [10 empty] | 2 | [8 empty] | 1 |  |  |  |  | 3 |  |  |  |  | 6
10 | 1 | 1 | [13 empty] | 1 | [9 empty] | 1 |  | 1 |  |  |  |  | 2 |  | 2
11 | 3 | [17 empty] | 1 | [7 empty] | 2 | [6 empty] | 4
12 | 1 | 1 | [10 empty] | 1 | [12 empty] | 1 | 1 | [6 empty] | 2 | 2
13 |  | 1 | [10 empty] | 1 | [12 empty] | 1 | [8 empty] | 2
14 | [28 empty] | 11
15,28,29 | [29 empty] | 3
16,30 | [30 empty] | 2
31 |  | 3 | [8 empty] | 1 | [17 empty] | 1
3//1 | 3 |  | 3 |  |  | 2 | 2 | 1 |  | 1 |  |  |  | 1 |  |  |  | 1 | 1 |  |  |  |  | 1 | 1 |  | 2 | 2 |  |  |  |  | 4 | 1 |  | 1
2,17,18 |  | 3 | [8 empty] | 3 | [14 empty] | 3 | [8 empty] | 6
3 |  | 2 | [8 empty] | 1 | [9 empty] | 1 |  |  |  |  | 1 | [8 empty] | 2
4,19,20,21 |  | 6 | [8 empty] | 6 | [14 empty] | 6 | [8 empty] | 12
5 | 1 | 1 | [10 empty] | 1 | [5 empty] | 1 | [6 empty] | 1 | [8 empty] | 2
6,24,25 |  | 3 | [13 empty] | 3 | [9 empty] | 3 | [8 empty] | 6
7 |  | 1 | [13 empty] | 1 | [9 empty] | 1 | [8 empty] | 2
8 |  | 2 | 1 | [12 empty] | 2 | [9 empty] | 2 | [8 empty] | 4
9,26,27 |  | 1 | [13 empty] | 3 | [9 empty] | 3 | [8 empty] | 6
10 |  | 2 | [8 empty] | 2 | [14 empty] | 2 | [8 empty] | 4
11 |  |  | 2 | [10 empty] | 1 |  |  |  |  | 1 | [8 empty] | 1 |  |  |  |  | 2
12 |  | 1 | 1 | [12 empty] | 1 |  |  | 1 | [6 empty] | 1 | [8 empty] | 2
13 | 1 | 1 | [10 empty] | 1 | [7 empty] | 1 |  |  |  |  | 1 | [8 empty] | 2
14 | 1 | [11 empty] | 1 | [12 empty] | 1 | [8 empty] | 2
15 | [5 empty] | 1 | [6 empty] | 1 | [7 empty] | 1 |  |  |  |  | 1 | [8 empty] | 2
16 | [28 empty] | 28
56,57,58,59 |  | 12 | [8 empty] | 4 | [17 empty] | 4
4//1 | 2 |  |  |  |  | 1 | 2 | 1 |  | 1 | [7 empty] | 1 | 1 |  |  |  |  | 1 | 1 |  | 2 | [6 empty] | 1 |  | 2
2 | 1 | 3 | 3 | [7 empty] | 1 |  |  | 1 | 1 | 1 | [9 empty] | 2 | 1 | 1 |  |  |  |  | 2 | 2 | 4
3 | 1 |  | 6 | 1 | [9 empty] | 1 | 2 | [11 empty] | 1 | 3 |  |  |  |  | 6 | 2
4,6,9,10 | [28 empty] | 4
11 | 1 | 3 | [10 empty] | 1 | [7 empty] | 1 |  |  |  |  | 2 | [8 empty] | 4
12 |  | 1 | [13 empty] | 1 | [9 empty] | 1 | [8 empty] | 2
8 |  | 2 | [8 empty] | 1 | [14 empty] | 2 | [8 empty] | 4
5 | 1 | 1 | 1 | [12 empty] | 1 |  |  | 1 | [6 empty] | 1 | 1 | [6 empty] | 2 | 2
5//1 | 3 |  |  |  |  | 1 | 2 | 1 |  | 1 | [7 empty] | 1 | 1 |  |  |  |  | 1 | 1 |  | 2 | [6 empty] | 1 |  | 2
2 | 1 |  | 4 | [8 empty] | 1 |  | 2 |  |  |  |  | 1 | [7 empty] | 2 | 2 |  |  |  |  | 4 | 4
3 |  | 1 | [13 empty] | 1 | [9 empty] | 1 | [8 empty] | 2
4 |  | 1 | [13 empty] | 1 | [9 empty] | 1 | [8 empty] | 2
5 |  | 1 | [8 empty] | 1 | [10 empty] | 1
6//1 |  | 2 | [8 empty] | 1 | [14 empty] | 2 | [8 empty] | 4
2 |  | 2 | [8 empty] | 1 | [14 empty] | 2 | [8 empty] | 4
3 |  | 2 | [8 empty] | 1 | [9 empty] | 1 |  |  |  |  | 1 | [8 empty] | 2
4 | 1 | 1 | [10 empty] | 1 | [12 empty] | 1 | 1 | [6 empty] | 2 | 2
5 | 3 | [11 empty] | 1 | [5 empty] | 1 | [6 empty] | 1 | 1 | [6 empty] | 2 | 2
6 | 2 |  | 8 |  |  |  | 2 | 1 | 1 |  |  |  |  | 2 | 1 |  |  | 2 | 1 |  |  |  |  | 1 | 1 |  | 2 | 2 |  |  |  |  | 5 | 2 |  | 2
7 | 1 | 1 | 2 | [11 empty] | 1 | 1 | [9 empty] | 1 | 1 | 1 |  |  |  |  | 2 | 2 | 2
8 | 1 | 1 | [10 empty] | 1 | [5 empty] | 1 | [6 empty] | 1 | [8 empty] | 2
9 | 1 | 1 | [10 empty] | 1 | [12 empty] | 1 | 1 | [6 empty] | 2 | 2
10 | 3 | 1 | [9 empty] | 2 | 1 | [12 empty] | 1 | 2 | [6 empty] | 4 | 2
11 |  | 6 | [8 empty] | 2 | [9 empty] | 2 |  |  |  |  | 3 | [8 empty] | 6
12,13,15 |  | 12 | [8 empty] | 6 | [14 empty] | 12 | [8 empty] | 24
14 |  | 2 | [8 empty] | 1 | [9 empty] | 1 |  |  |  |  | 1 | [8 empty] | 2
17 |  | 1 | [10 empty] | 1 | [12 empty] | 1 | [8 empty] | 2
18 |  | 2 | [8 empty] | 1 | [9 empty] | 1 |  |  |  |  | 1 | [8 empty] | 2
20 |  | 1 | [8 empty] | 1 | [14 empty] | 1 | [8 empty] | 2
22 |  | 2 | [8 empty] | 1 | [14 empty] | 2 | [8 empty] | 4
49 | 2 | [10 empty] | 1 | [14 empty] | 2 | [6 empty] | 4
23,24,25 | [28 empty] | 26
7//1 | [26 empty] | 1 | [6 empty] | 2
2 | 2 | [10 empty] | 1 | [14 empty] | 2 | [6 empty] | 4
3 |  | 2 | [8 empty] | 1 | [9 empty] | 1 |  |  |  |  | 1 | [8 empty] | 2
4,6 | 4 | 2 | [9 empty] | 2 | [8 empty] | 2 |  |  |  |  | 2 | 2 | [6 empty] | 4 | 4
5 | [28 empty] | 4
8 |  | 2 | [8 empty] | 1 | [14 empty] | 2 | [8 empty] | 4
10 | 1 | [10 empty] | 1 | [14 empty] | 2 | [6 empty] | 4
11 |  | 1 | [10 empty] | 1 | [12 empty] | 1 | 1 | [6 empty] | 2 | 2
12 | 1 | [10 empty] | 1 | [14 empty] | 1 | [6 empty] | 2
8//1,3,5 | [28 empty] | 5
2 |  | 3 | [8 empty] | 1 | [9 empty] | 1 |  |  |  |  | 2 | [8 empty] | 4
4 |  | 1 | 1 | [12 empty] | 1 | [9 empty] | 1 |  | 1 |  |  |  |  | 2 |  | 2
6,7 |  | 2 | [13 empty] | 2 | [9 empty] | 2 | [8 empty] | 4
8,10 | 10 | 2 | [9 empty] | 4 | 2 | [12 empty] | 2 | 6 | [6 empty] | 12 | 4
13 | 1 |  | 1 | [11 empty] | 1 | [11 empty] | 1 | 1 |  |  |  |  | 2 | 2
12 | [25 empty] | 1 | [8 empty] | 2
14 | 1 |  |  |  |  | 1 | [20 empty] | 1 | [6 empty] | 2
15 |  | 3.5 | [8 empty] | 1 | [17 empty] | 1
9//1 | 2 | 6 | 5 | 1 | 1 | [8 empty] | 1 |  | 2 |  | 2 | [6 empty] | 1 | 2 | 2 | 1 |  |  |  |  | 2 | 2 | 4
2 |  | 2 | [8 empty] | 1 | [9 empty] | 1 |  |  |  |  | 1 | [8 empty] | 2
3 | 1 | [10 empty] | 1 | 1
4 | 2 | 1 | [9 empty] | 1 | [13 empty] | 1 | 1 | [6 empty] | 2 | 2
5 | [29 empty] | 1
6 | 1 | [10 empty] | 1 | [14 empty] | 1 | [6 empty] | 2
7 |  | 2 | [8 empty] | 1 | [14 empty] | 2 | [8 empty] | 4
8 | 1 | [10 empty] | 1 | [14 empty] | 1 | [6 empty] | 2
9 | 3 | [10 empty] | 1 | [14 empty] | 2 | [6 empty] | 4
10 | 1 |  | 1 | [11 empty] | 1 | [11 empty] | 1 | 1 |  |  |  |  | 2 | 2
11 | 2 | [10 empty] | 1 | [14 empty] | 2 | [6 empty] | 4
12 |  | 1 | 1 | [12 empty] | 1 | [9 empty] | 1 |  | 1 |  |  |  |  | 2 |  | 2
13,14 | [28 empty] | 2
16 |  | 3 | [10 empty] | 1 | [15 empty] | 1
15 | [20 empty] | 1
10//1 | 8 | 1 | 1 | 1 |  | 1 | 2 | 1 |  |  |  | 1 | 1 |  | 1 |  |  | 1 | 1 |  |  |  |  | 1 | 1 | 1 | 3 | 1 |  |  |  |  | 2 | 5 | 2 | 2
2 | 4 | 1 | 1 | [8 empty] | 1 | 1 |  | 1 | [10 empty] | 1 | 2 | 1 |  |  |  |  | 2 | 4 | 2
3 | 7 | [10 empty] | 3 | [6 empty] | 1 | [7 empty] | 4 | [6 empty] | 8
8 | 4 |  |  |  |  | 1 | [5 empty] | 1 | [14 empty] | 2 | [6 empty] | 4
4 | 2 | [10 empty] | 1 | [14 empty] | 2 | [6 empty] | 4
6 | 1 | 1 | [10 empty] | 1 | [12 empty] | 1 | 1 | [6 empty] | 2 | 2
5 | 2 | [10 empty] | 1 | [14 empty] | 2 | [6 empty] | 4
7,10 | [28 empty] | 2
11 |  |  |  |  | 1
12 | 2 | [10 empty] | 1 | [14 empty] | 2 | [6 empty] | 4
9 | 2 | 3 | [8 empty] | 1 | 1 | [8 empty] | 2 |  |  |  |  | 3 | [8 empty] | 6
| 141 | 163.9 | 60 | 3 | 2 | 12 | 14 | 7 | 2 | 3 | 56 | 33 | 24 | 15 | 9 | 27 | 1 | 10 | 17 | 2 | 22 | 1 | 1 | 7 | 8 | 130 | 82 | 29 | 108 | 4 | 3 | 1 | 55 | 145 | 260 | 12

## B.O.Q
SAMPLE BOQ
Bill No. 07
Laying of DI / uPVC pipes, specials, fittings and DI CI valves for Distribution Main
Item No. | CESSM3 Code No. | Description | Unit | Qty. | Rate Rs: Cts: | Amount Rs: Cts:
CLASS I PIPE WORK - PIPES
|  | LAYING AND FIXING OF PVC/DI PIPES AND FITTINGS |  |  |  | `
Rate to be included for cutting of asphalt layer by using asphalt cutter, where nesassary excavation, making trial holes, backfilling pipe trenches, disposal of excavated materials, cutting and grinding of pipes, laying and jointing of pipes, shoring and dewatering where necessary. Supplying and installation of gauge 250 polythene sleeving to all DI pipes with before laying. Rate to include for cleaning and disinfections, pressure testing of pipes and laying marker tape.
PVC socket and spigot pipes with push fit joints in trenches depth not exceeding 1.5m for Normal ground.
1 | I522 | 225 mm dia. Pipes (Type 600) | m
2 | I512 | 160 mm dia. Pipes (Type 600) | m
3 | I512 | 110 mm dia. Pipes (Type 600). | m
4 | I512 | 90 mm dia. Pipes (Type 600). | m
PVC socket and spigot pipes with push fit joints in trenches depth not exceeding 1.5m for road crossing.
5 | I512 | 160 mm dia. Pipes | m
6 | I512 | 110 mm dia. Pipes | m
7 | I512 | 90 mm dia. Pipes | m
CLASS J : PIPE WORK -
FITTINGS AND VALVES
FIXING OF FITTINGS
P.V.C double Socket Bend.
160 mm dia.
8 | J411 | 90 deg. Bend | nr
9 | J411 | 221/2 deg. Bend | nr
10 | J411 | 45 deg. Bend | nr
110 mm dia.
11 | J411 | 90 deg. Bend | nr
12 | J411 | 221/2 deg. Bend | nr
13 | J411 | 45 deg. Bend | nr
90 mm dia.
14 | J411 | 90 deg. Bend | nr
15 | J411 | 221/2 deg. Bend | nr
16 | J411 | 45 deg. Bend | nr
LAYING AND JOINTING OR FIXING OF PVC / DI PIPES, SPECIALS, FITTINGS AND VALVES AT JUNCTIONS.
Rate to be included for concrete trust blocks and all necessary items of work required for complete the fixing.
(Refer Drawings)
P.V.C double Socket Bend.
17 | J411 | 160mm 90 deg. Bend | nr
18 | J411 | 110 mm 90 deg. Bend | nr
19 | J411 | 90 mm 90 deg. Bend | nr
P.V.C double Socket Tee.
20 | J421 | 90 x 90 mm dia. | nr
21 | J421 | 110 x 90 mm dia. | nr
22 | J421 | 110 x 110 mm dia. | nr
23 | J421 | 160 x 160 mm dia. | nr
24 | J421 | 160 x 110 mm dia. | nr
25 | J421 | 160 x 90 mm dia. | nr
P.V.C Redusing socket.
26 | J432 | 225 - 160 mm dia. | nr
27 | J432 | 160 - 110 mm dia. | nr
28 | J432 | 160 - 90 mm dia. | nr
29 | J431 | 110 - 90 mm dia. | nr
30 | J431 | 90 - 63 mm dia. | nr
D.I Double Flanged Taper
31 | J331 | 200 - 100 mm dia. | nr
32 | J331 | 150 - 100 mm dia. | nr
33 | J351 | 200 mm dia. Flanged Adaptor to suit 225 mm dia. P.V.C pipe | nr
Flexible Mecanical Coupling
34 | J390 | 80 mm dia. | nr
P.V.C End cap
35 | J491 | 90 mm dia | nr
36 | J491 | 110 mm dia | nr
37 | J491 | 160 mm dia | nr
FIXING OF VALVES AND FITTINGS
Rate to included for additional excavation, shoring, dewatering, preparation of surfaces, disposal of excavated materials, upholding sides of excavation, backfilling, thrust blocks for fittings and all necessary items of work required for completion of work
In line Sluice Valves (Detail as shown in Drawing 816 -04 -77- ME-3031/3041).
38 | J811 | 150 mm dia | nr
39 | J811 | 100 mm dia | nr
40 | J811 | 80 mm dia. | nr
41 | J481 | 110 mm dia. P.V.C protection tube1.0 m long approx. | nr
Flanged Adaptor for Inline Valves
42 | J351 | 100 mm dia. Flanged Adaptor to suit 110 mm dia. P.V.C pipe | nr
43 | J351 | 150 mm dia. Flanged Adaptor to suit 160 mm dia. P.V.C pipe | nr
44 | J351 | 80 mm dia. Flanged Adaptor to suit 90 mm dia. P.V.C pipe | nr
D.M.A Meter Instalation. (Detail as shown in Drawing 816 -04 -77- ME-3041)
45 | J890 | 100 mm dia. Flanged Meter | nr
46 | J811 | 100 mm dia. Pressure redusing valve. | nr
47 | J381 | 100 mm dia. D.I Flanged and plain ended pipe (1000 mm long) | nr
48 | J381 | 100 mm dia. D.I double Flanged pipe (500 mm long) | nr
49 | J900 | 100 mm dia. D.I Coupling | nr
Pressure Tapping
50 | J900 | 110 mm dia. Saddle with quickfit | nr
51 | J900 | 90 mm dia. Saddle with quickfit | nr
52 | J482 | 160 mm dia. P.V.C protection tube. | nr
AIR VALVE
Air Valves complete as shown in detail on drawing No: 816-04-77-ME-3025
50 | J861 | 25 mm dia. Single orifice scrwed down type air valve with isolating cock as discribed in the specification to suit for pipes and fittings manufactured to ISO2531/ BSEN545 | nr
P.V.C Clamp saddle with 32mm dia. Branch
51 | J491 | To suit to 160 mm dia. P.V.C Clamp saddle. | nr
52 | J491 | To suit to 110 mm dia. P.V.C Clamp saddle. | nr
53 | J491 | To suit to 90 mm dia. P.V.C Clamp saddle. | nr
52 | J491 | 160 mm dia. Repair socket | nr
53 | J491 | 110 mm dia. Repair socket | nr
54 | J491 | 90 mm dia. Repair socket | nr
WASHOUT VALVES
Detail shown in Drawing No: 816-04-77-ME-3027.
55 | J821 | 80 mm dia. D.I Flanged Sluice valve. | nr
56 | J421 | 160 x 90 mm dia. P.V.C socketed tee | nr
57 | J421 | 110 x 90 mm dia. P.V.C socketed tee | nr
58 | J421 | 90 x 90 mm dia. P.V.C socketed tee | nr
59 | J411 | 90 mm dia. P.V C 45 deg.socketed bend. | nr
60 | J481 | 90 mm dia. P.V.C pipe piece 200mm long. | nr
61 | J351 | Flanged adaptor to suit 90 mm dia. P.V.C pipe | nr
62 | J481 | 90 mm dia. P.V.C pipe piece 3.0m long approx. | nr
CLASS K : PIPE WORK
MANHOLE AND PIPE WORK ANCILLARIES
Construction of Valve chambers and pipe work ancillaries
Rate to be included for excavation, preparation of surfaces, disposal of excavated materials, upholding sides of excavation, back filling, concrete, reinforcement, formwork, joints and finishes, dewatering and other related items.
Air Valve Chamber
63 | K232 | Concrete grade 25 valve chamber as shown in detail Drawing No :816-04-77 -ME-3025 of internal dimension 850 x850 mm and average depth 2000 with walls 125 mm thick. built on 1100 x 1100 x 200 mm base slab. | nr
The base slab to be provided with 75 mm thick Grade 10 screed concrete.. The base and walls shall be reinforced with 10 mm dia. tor steel bars and chamber to be fixed with supply and fixing of 600 mm dia. heavy duty DI man hole cover and frame as specified and complete as directed.
Bitumen pad and concrete grade 20 surround shall also be provided as directed and as shown on drawing. Rate to be included for hot dipped galvanized mild steel steps and suitable concrete support for valve.
Inline Valve /Presure redusing valve/Meter chamber
64 | K232 | Concrete grade 25 valve chamber as shown in detail Drawing No:816-04-77-ME-3041 of internal dimension 2000 x 850 mm and average depth 2000 with walls 125 mm thick. built on 2250 x1100 mm base slab. The base slab to be provided with 75 mm thick Grade 10 screed concrete.. The base and walls shall be reinforced with 10 mm dia. tor steel bars and chamber to be fixed with supply and fixing of 700 x 1000 mm heavy duty DI manhole cover and frame as specified and complete as directed. Bitumen pad and concrete grade 20 surround shall also be provided as directed and as shown on drawing. Rate to be included for hot dipped galvanized mild steel steps and Grade 20 suitable concrete block support for valve. | nr
Meter Chamber
65 | K232 | Concrete grade 25 valve chamber as shown in detail Drawing No:816-04-77-ME-3030 of internal dimension 1000 x 850 mm and average depth 2000 with walls 125 mm thick. built on 1250 x1100 mm base slab. The base slab to be provided with 75 mm thick Grade 10 screed concrete.. The base and walls shall be reinforced with 10 mm dia. tor steel bars and chamber to be fixed with supply and fixing of 600 mm dia. heavy duty DI manhole cover and frame as specified and complete as directed. Bitumen pad and concrete grade 20 surround shall also be provided as directed and as shown on drawing. Rate to be included for hot dipped galvanized mild steel steps and Grade 20 suitable concrete block support for valve. | nr
Outfall Chamber
66 | K232 | Concrete grade 25 outfall chamber as shown in detail Drawing No: 816 -04 -77 ME-3027 of internal dimension 850 x 850 mm and average depth 2000 with walls 125 mm thick. built on 1100 x 1100 x 200 mm base slab. The base slab to be provided with 75 mm thick Grade 10 screed concrete.. The base and walls shall be reinforced with 10 mm dia. tor steel bars and chamber to be supply & fixed of 600 mm heavy duty DI manhole cover and frame as specified and complete as directed. Bitumen pad and concrete grade 20 surround shall also be provided and as directed. Rate to be included hot dipped galvanized mild steel steps ,300 x300 x10 mm thk Galvanized MS plate and 6.3 dia. M.S lugs welded to the galvanized plate as shown on drawing. | nr
Culvert crossings
Laying and jointing or fixing in position DI/PVC pipes specials, fittings, valves and other materials as shown in drawing. Rate to be included for excavation, shoring, diversion of water ways providing suitable anchor blocks and all other necessary materials to complete the crossing. Rate to be included for supplying and laying hume pipe encasing, rubble and sand packing etc. where necessary.
Crossing Type 1 for P.V.C Main as shown on drawing No 816-04-77-ME-3029
67 | K 621 | 150 mm dia. DI plain ended pipe to suit Main pipe line(length of crossing - 3.2m) | nr
68 | K 621 | 150 mm dia. DI plain ended pipe to suit Main pipe line(length of crossing - 3.0m) | nr
69 | K 621 | 100 mm dia. DI Plain ended pipe to suit Main pipe line (length of crossing - 3.0 m) | nr
70 | K 621 | 80 mm dia. DI Plain ended pipe to suit Main pipe line (length of crossing - 3.9 m) | nr
71 | K 621 | 80 mm dia. DI Plain ended pipe to suit Main pipe line (length of crossing - 3.8 m) | nr
72 | K 621 | 80 mm dia. DI Plain ended pipe to suit Main pipe line (length of crossing - 3.5 m) | nr
73 | K 621 | 80 mm dia. DI Plain ended pipe to suit Main pipe line (length of crossing - 3.0 m) | nr
Crossing Type 2 for P.V.C Main as shown on drawing No 816-04-77-ME-3029
74 | K 621 | 150 mm dia. DI Plain ended pipe to suit main pipe line.(length of crossing - 4.8m) | nr
75 | K 621 | 150 mm dia. DI Plain ended pipe to suit main pipe line.(length of crossing - 4.3m) | nr
76 | K 621 | 150 mm dia. DI Plain ended pipe to suit main pipe line.(length of crossing - 3.9 m) | nr
77 | K 621 | 150 mm dia. DI Plain ended pipe to suit main pipe line.(length of crossing - 3.8m) | nr
78 | K 621 | 150 mm dia. DI Plain ended pipe to suit main pipe line.(length of crossing - 3.6m) | nr
79 | K 621 | 100 mm dia. DI Plain ended pipe to suit main pipe line.(length of crossing -4.8 m) | nr
80 | K 621 | 100 mm dia. DI Plain ended pipe to suit main pipe line.(length of crossing - 3.0 m) | nr
81 | K 621 | 80 mm dia. DI Plain ended pipe to suit main pipe line.(length of crossing - 5.4 m) | nr
82 | K 621 | 80 mm dia. DI Plain ended pipe to suit main pipe line.(length of crossing -4.6 m) | nr
83 | K 621 | 80 mm dia. DI Plain ended pipe to suit main pipe line.(length of crossing - 3.3 m) | nr
84 | K 621 | 80 mm dia. DI Plain ended pipe to suit main pipe line.(length of crossing - 3.0 m) | nr
Bridge Crossing .
Laying and jointing or fixing in position D.I pipes, specials, fittings, valves and other materials as shown in detail on drawings. Rate to be included for breaking through abutments / wing walls if found necessary, additional excavation, shoring, diversion of water ways, providing suitable anchor blocks, and all other necessary materials to complete the crossing.
85 | K631 | Bridge crossing for 16.0.m wide river, complete with 150 mm dia D.I pipes complete as shown in detail drawing No: 816-03-77-ME 3117. | nr
86 | K631 | Bridge crossing for 10.0 m wide river, complete with 150 mm dia D.I pipes complete as shown in detail drawing No: 816 -03 - 77 ME3125. | nr
Reinstatement
Temporary reinstatement of roads
Temporary reinstatement to be done accordance with specification and the guidance of PRDA. (Rate to be included for prepare the earth shoulder and maintaining road surface until handling over to Provincial Road Authorities / PS.) Detail as shown in Drawing No: W301/01.
87 | K711 | 225 mm dia. PVC pipe | m
88 | K711 | 160 mm dia. PVC pipe | m
89 | K711 | 110 mm dia. PVC pipe | m
90 | K711 | 90 mm dia. PVC pipe | m
91 | K 79 | Provisional sum for reinstatement of unidentified damages to private properties, which are not covered by the third party insurance, with the prior approval of the Engineer. | Provisional Sum
Marker Post
92 | K82 | Supply and installation of valve indicator post at each chamber and surface box location. Indicator shall be pre - cast concrete grade. | nr
CLASS L - PIPE WORK
SUPPORTS AND PROTECTION ANCILLARIES TO LAYING AND EXCAVATION
Rate to be included for excavation, preparing of surfaces, disposal of excavated material, upholding sides of excavation and dewatering.
93 | L111 | Extras to excavation for hard rock in pipe trench. | m3
94 | L111 | Extras to excavation for soft disintegrated rock in pipe trench. | m3
95 | L119 | Extras to backfilling in pipe trenches with imported soil (Refer Drg. No: W301/01.) | m3
96 | L711 | Suitable Concrete Gr.10 Block support for valve | nr
97 | L710 | 450 x 450 x 100 mm size Grade 20 pre cast concrete block with 110 mm dia. Opening at centere for valve protection tube. | nr
98 | L711 | Concrete grade 20 thrust blocks for 160 mm dia. P.V.C socketed 90 deg. bends.( concrete volume –0.033m3 per each.) | nr
99 | L711 | Concrete grade 20 thrust blocks for 160 mm dia. P.V.C socketed 45deg. bends.( concrete volume –0.020m3 per each.) | nr
100 | L711 | Concrete grade 20 thrust blocks for 160 mm dia. P.V.C socketed 221/2 deg. bends.( concrete volume –0.013m3 per each.) | nr
101 | L711 | Concrete grade 20 thrust blocks for 110 mm dia. P.V.C socketed 221/2 deg. bends.( concrete volume –0.007m3 per each.) | nr
102 | L711 | Concrete grade 20 thrust blocks for 110 mm dia. P.V.C socketed 45 deg. bends.( concrete volume –0.010m3 per each.) | nr
103 | L711 | Concrete grade 20 thrust blocks for 110 mm dia. P.V.C socketed 90 deg. bends.( concrete volume –0.017m3 per each.) | nr
104 | L712 | Concrete grade 20 thrust blocks for 90 mm dia. P.V.C socketed 221/2 deg. bends.( concrete volume –0.007m3 per each.) | nr
105 | L713 | Concrete grade 20 thrust blocks for 90 mm dia. P.V.C socketed 45 deg. bends.( concrete volume –0.010m3 per each.) | nr
106 | L714 | Concrete grade 20 thrust blocks for 90 mm dia. P.V.C socketed 90 deg. bends.( concrete volume –0.017m3 per each.) | nr
Wrapping Flanged Joints with mastic material and primer compound.
107 | L902 | 200mm dia. D.I Pipe | nr
108 | L901 | 150 mm dia. D.I Pipe | nr
109 | L901 | 100 mm dia. D.I Pipe | nr
110 | L901 | 80mm dia. D.I Pipe | nr
CLASS L :PIPE WORK
Supports and protection, ancillaries to laying and excavation
Rate to be included for excavation, preparing of surfaces, disposal of excavated material, upholding sides of excavation and dewatering.
PIPE BEDDINGS (Detail as shown in Drawing No: W301/02.
Type A (Normal soil)
111 | L512 | Surround in pipe with fill of quarry dust/ Mined sand compacted and pipe normal bore 200 - 300 mm. | m
112 | L511 | Surround in pipe with fill of quarry dust/ Mined sand compacted and pipe normal bore not exceedind 200 mm. | m
Type B (Normal soil)
113 | L532 | Surround in pipe fill of earth or partical size not greater than 25 mm with the properties PL<15,LL<40,CBR>20 with pipe normal bore 200 - 300 mm. | m
114 | L531 | Surround in pipe fill of earth or partical size not greater than 25 mm with the properties PL<15,LL<40,CBR>20 with pipe normal bore not exceedind 200mm.mm | m
Type C (Loose Soil)
115 | L332 | Beds in pipe trenches with compacted crushed stone (>6mm) with pipe normal bore 200 - 300 mm. | m
116 | L331 | Beds in pipe trenches with compacted crushed stone (>6 mm) | m
117 | L531 | Surround in pipe with fill of quarry dust/ Mined sand compacted with pipe normal bore not exceeding 200mm. | m
118 | L532 | Surround in pipe with fill of quarry dust/ Mined sand compacted pipe normal bore 200 - 300 mm. | m
CLASS – N
MISCELLANEOUS METAL WORK
119 | N190 | Supply and Fixing of 100 x100 x 80 mm D.I surface box with 110 mm square clear opening at centre. Rate to include for concrete Grade 20 surround. | nr
120 | N190 | Supply and Fixing of 100 x100 x 80 mm D.I surface box with 110 mm square clear opening at centre. Rate to include for concrete Grade 20 surround. | nr
Note on A152: Administrator: